## Instructions
Calculator for Retrofit Lighting Measures
***This calculator is used for estimating savings and incentives from the installation of prescriptive lighting measures. The measure inputs used in this calculator, by an applicant, will be reviewed by the Program in order to determine the final incentive amount. The Program reserves the right to inspect any and all measures prior to any incentive payment.
Description
This calculator will be used to calculate energy savings, demand savings, and incentive amounts for the following lighting measures.
Fixtures
Measure Category | Measure
LED Troffer Luminaires | New LED linear recessed troffer/panel for 2x2 and 1x4 luminaires
LED Troffer Luminaires | New LED linear recessed troffer/panel for 2x4 luminaires
LED Flat Panel Luminaires | New LED flat panel for 2x2 and 1x4 luminaires
LED Flat Panel Luminaires | New LED flat panel for 2x4 luminaires
LED Linear Ambient/Stairwell Luminaires | New LED Linear ambient luminaire with direct and indirect components or Vapor Tight, min. IP65
LED Linear Ambient/Stairwell Luminaires | New LED linear ambient luminaire
LED Linear Ambient/Stairwell Luminaires | New LED stairwell luminaire
LED Interior Directional Luminaires | New LED wall wash luminaire
LED Interior Directional Luminaires | New LED track/mono-point luminaire
LED Display Case Luminaires | New LED display case luminaire
LED Display Case Luminaires | New LED display case luminaire installed in reach-in coolers/freezers
LED High/Low Bay Luminaires | New LED high/low bay luminaire - DLC reported lumens between 5,000 lm - 9,999 lm
LED High/Low Bay Luminaires | New LED high/low bay luminaire - DLC reported lumens between 10,000 lm - 19,999 lm
LED High/Low Bay Luminaires | New LED high/low bay luminaire - DLC reported lumens between 20,000 lm - 29,999 lm
LED High/Low Bay Luminaires | New LED high/low bay luminaire - DLC reported lumens between 30,000 lm - 39,999 lm
LED High/Low Bay Luminaires | New LED high/low bay luminaire - DLC reported lumens 40,000 lm or more
LED Exterior Luminaires | New LED exterior luminaire - DLC reported lumens 4,999 lm or less
LED Exterior Luminaires | New LED exterior luminaire - DLC reported lumens between 5,000 lm - 9,999 lm
LED Exterior Luminaires | New LED exterior luminaire - DLC reported lumens between 10,000 lm - 19,999 lm
LED Exterior Luminaires | New LED exterior luminaire - DLC reported lumens between 20,000 lm - 29,999 lm
LED Exterior Luminaires | New LED exterior luminaire - DLC reported lumens between 30,000 lm - 39,999 lm
LED Exterior Luminaires | New LED exterior luminaire - DLC reported lumens 40,000 lm or more
LED Retrofit Kits | LED linear retrofit kit for 2x2 and 1x4 fixtures
LED Retrofit Kits | LED linear retrofit kit for 2x4 fixtures
LED Retrofit Kits | LED integrated retrofit kit for 2x2 and 1x4 fixtures
LED Retrofit Kits | LED integrated retrofit kit for 2x4 fixtures
LED Retrofit Kits | LED integrated flat panel retrofit kit for 2x2 and 1x4 fixtures
LED Retrofit Kits | LED integrated flat panel retrofit kit for 2x4 fixtures
LED Retrofit Kits | LED retrofit kit for linear ambient luminaire
LED Retrofit Kits | LED retrofit kit for high/low bay luminaire
LED Retrofit Kits | LED retrofit kit for exterior luminaire
LED ENERGY STAR Fixtures | New LED ENERGY STAR fixture - 1,499 lm or less
LED ENERGY STAR Fixtures | New LED ENERGY STAR fixture - 1,500 lm - 2,999 lm
LED ENERGY STAR Fixtures | New LED ENERGY STAR LED fixture - 3,000 lm or greater
LED Replacement Lamps | LED linear replacement lamp with new LED driver
LED Replacement Lamps | LED pin-base replacement lamp for CFL
LED Replacement Lamps | LED A lamp
LED Replacement Lamps | LED BR/R lamp
LED Replacement Lamps | LED Decorative or Globe lamp
LED Replacement Lamps | LED MR lamp
LED Replacement Lamps | LED PAR lamp - PAR20
LED Replacement Lamps | LED PAR lamp - PAR30 & PAR38
LED Replacement Lamps | LED mogul-screw base replacement for HID lamps and new external driver
Exit Signs | LED Exit Sign replacing incandescent or fluorescent
Linear Fluorescents | High Performance T8 Lamps or Fixtures replacing standard T8 lamps or fixtures
Street & Area Lighting | LED Street & Area Lighting replacing less efficient technology
Other | Lighting - Other
Custom | Lighting - Custom
Controls
Measure Category | Measure
Networked Lighting Controls | Networked lighting control system controlling efficient luminaires (Min. Watts Controlled = 200)
Networked Lighting Controls | Networked lighting control w/local or cloud server required
Networked Lighting Controls | Networked lighting control - w/local or cloud server required - lower wattage fixtures/downlights (Min. Watts Controlled = 20)
Networked Lighting Controls | Networked lighting control no server required
Networked Lighting Controls | Networked lighting control no server required - lower wattage fixtures/downlights (Min. Watts Controlled = 20)
Dual Daylight/Occupancy Controls | Dual daylight & occupancy sensor (DOS) (Min. Watts Controlled = 150)
Dual Daylight/Occupancy Controls | Dual daylight & occupancy sensor (DOS) - lower wattage fixtures/downlights (Min. Watts Controlled = 20)
Daylight Controls | Daylight continuous dimming control (Min. Watts Controlled = 150)
Daylight Controls | Daylight continuous dimming control - lower wattage fixtures/downlights (Min. Watts Controlled = 20)
Occupancy/Vacancy Controls | Vacancy control (Min. Watts Controlled = 150)
Occupancy/Vacancy Controls | Vacancy control - lower wattage fixtures/downlights (Min. Watts Controlled = 20)
Occupancy/Vacancy Controls | Occupancy control (Min. Watts Controlled = 150)
Occupancy/Vacancy Controls | Occupancy control - lower wattage fixtures/downlights (Min. Watts Controlled = 20)
Input Instructions
Use the color coded reference cells. Only yellow cells need input.
Requires Input
Doesn't Need an Input
Output Cell
Project Info & Summary
Begin at the "Project Info & Summary" tab to fill in general project and customer information. Fill in all yellow cells.
a) Project Info
| Contractor: | Name or Company Name of Trade Ally or Contractor.
| Customer Name: | Name of customer as corroborated by the submitted W9.
| Customer Contact Name: | Name of on-site contact (plant manager, maintenance staff personnel etc.).
| Customer Contact Phone: | Phone number to reach the on-site contact.
| Customer Contact Email: | Email address to reach on-site contact, if available.
| Project Site Name: | Specific site name where project will be installed
| Project Site Address: | Specific address of the site where project will be installed
| City: | Specify the city in which project is located.
| ZIP Code: | Specify the zip code of the project site
| Installation Date:* | Enter the date lighting installations were completed.
| Electric Rate ($/kWh)* | Rate of electricity for the project site. Can be estimated from utility bills. Click here for additional information.
| Demand Rate ($/kW)* | Rate of demand for the project site. Can be estimated from utility bills. See PDF for additional information.
| Total Project Cost:* | Total installation cost for the submitted project scope (includes material and labor).
| Building Type (Select from list):* | Select the appropriate building type from this dropdown list.
b) Savings & Incentive Summary
Fixtures:
| Change in Connected Load | Estimated gross reduction in lighting load in kW.
| DkWUtility | Estimated peak demand savings from the utility perspective.
| DkWPJM Summer | Estimated average demand savings during the PJM Summer Performance Period.
| DkWPJM Winter | Estimated average demand savings during the PJM Winter Performance Period.
| DkWh | Estimated annual energy savings.
Controls:
| DkWUtility | Estimated peak demand savings from the utility perspective.
| DkWPJM Summer | Estimated average demand savings during the PJM Summer Performance Period.
| DkWPJM Winter | Estimated average demand savings during the PJM Winter Performance Period.
| DkWh | Estimated annual energy savings.
Total:
| Estimated SC Peak Demand Savings (kW) | Estimated peak demand savings from the utility perspective.
| DkWPJM Summer | Estimated average demand savings during the PJM Summer Performance Period.
| DkWPJM Winter | Estimated average demand savings during the PJM Winter Performance Period.
| Estimated Annual Energy Savings (kWh) | Estimated annual energy savings.
| Fixture Equipment Cost | Total reported equipment cost for fixture measures installed.
| Controls Equipment Cost | Total reported equipment cost for controls measures installed.
| Fixture Incentive | Estimated total incentive for fixture measures.
| Controls Incentive | Estimated total incentive for controls measures.
| Equipment Cost ($) | Estimated total equipment cost.
| Estimated Incentive ($) | Estimated total incentive.
Calculator
Use the "Calculator" tab to create an inventory of all measures. Required inputs are in yellow.
| Interior/ Exterior | Select "Interior" or "Exterior" from the dropdown.
| Floor | Enter the floor number where the measure is installed.
| Area Description | Enter a description of the space where the measure is installed. Area descriptions should provide detail sufficient for inspection purposes.
| Exterior Lighting Description (Exterior Lighting Only) | For exterior measures, enter a description of the space where the measure is installed. Exterior lighting descriptions should provide detail sufficient for inspection purposes.
| Space Type | Select the space type from the dropdown. The dropdown list is dependent upon the building type selected. If the measure is installed in a space type that is not shown, select "Other".
| Space Cooling Type | Select the type of cooling for the space where the measure is installed.
| Space Heating Type | Select the type of heating for the space where the measure is installed.
| Measure Category | Select the measure category that corresponds to the fixture/controls installed.
| Measure | Select the measure that corresponds to the fixture/controls installed.
Pre | Fixture Code | Enter or select from the dropdown the fixture code the corresponds to the fixture type being removed/retrofitted.
| Quantity | Enter the quantity of fixtures being removed/retrofitted.
| Controls | Select the existing control type from the dropdown.
Post | Unique Fixture Identifier | Enter a unique fixture identifier for the fixtures being installed. NOTE: the incentive will NOT populate without an entry.
| Fixture Code | Enter or select from the dropdown the fixture code the corresponds to the fixture type being installed. Custom fixtures can be configured on the "Fixture Codes" tab starting on row 919.
| Quantity | Enter the quantity of fixtures being installed.
| Controls | Select the new control type from the dropdown.
| Sensors Installed | If controls were installed, enter the quantity of sensors installed.
Fixtures | Change in Connected Load | Estimated gross reduction in lighting load in kW.
| ΔkWUtility | Estimated peak demand savings from the utility perspective.
| ΔkWh | Estimated annual energy savings.
Controls | ΔkWUtility | Estimated peak demand savings from the utility perspective.
| ΔkWh | Estimated annual energy savings.
Total | ΔkWUtility | Estimated peak demand savings from the utility perspective.
| ΔkWh | Estimated annual energy savings.
| Fixture Equipment Cost | Total reported equipment cost for fixture measures installed.
| Controls Equipment Cost | Total reported equipment cost for controls measures installed.
| Fixture Incentive | Estimated total incentive for fixture measures.
| Controls Incentive | Estimated total incentive for controls measures.
| Total Incentive | Estimated total incentive.
Prescriptive Rebate Table | List of Prescriptive Retrofit Lighting Measures and associated incentive rates.
Fixture Codes | List of Fixture Codes for use in the calculator. "Custom" fixture codes can be entered starting on row 919.
| Tube Length | Length of fixture in inches. This is required to calculate incentives based on fixture length.
Report | Coming SOON

## Methodology (hidden)
Calculator Methodology
Fixture Measures
Change in Connected Load calculated using:
Demand savings calculated using:
where,
ISR is the In Service Rate
WHFd is the relevant demand waste heat factor (Utility, PJM Summer, PJM Winter)
CF is the relevant coincidence factor (SSP, PJM Summer, PJM Winter)
Energy savings calculated using:
where,
ISR is the In Service Rate
WHFe is the relevant energy waste heat factor
HOURS is the annual hours of use
Controls Measures
Demand savings calculated using:
where,
ISR is the In Service Rate
WHFd is the relevant demand waste heat factor (Utility, PJM Summer, PJM Winter)
CF is the relevant coincidence factor (SSP, PJM Summer, PJM Winter)
PostSVGd is the demand savings factor associated with the installed controls
PreSVGd is the demand savings factor associated with the existing controls
Energy savings calculated using:
where,
ISR is the In Service Rate
WHFe is the relevant energy waste heat factor
HOURS is the annual hours of use
PostSVGe is the energy savings factor associated with the installed controls
PreSVGe is the energy savings factor associated with the existing controls
Annual Fossil Fuel Savings Algorithm
Note: only applies if retrofit space is heated with fossil fuels. Negative value denotes increased fossil fuel consumption.
where,
AR is the Aspect Ratio
C is the constant to convert kWh to MMBtu
LHF is the fraction of lighting heat that contributes to space heating
Eff is the assumed heating system efficiency
𝐶ℎ𝑎𝑛𝑔𝑒 𝑖𝑛 𝐶𝑜𝑛𝑛𝑒𝑐𝑡𝑒𝑑 𝐿𝑜𝑎𝑑(𝑘𝑊)=((𝑃𝑟𝑒𝐹𝑖𝑥𝑡𝑢𝑟𝑒𝑄𝑡𝑦 ∗𝑃𝑟𝑒𝐹𝑖𝑥𝑡𝑢𝑟𝑒𝑊𝑎𝑡𝑡𝑠)−(𝑃𝑜𝑠𝑡𝐹𝑖𝑥𝑡𝑢𝑟𝑒𝑄𝑡𝑦 ∗𝑃𝑜𝑠𝑡𝐹𝑖𝑥𝑡𝑢𝑟𝑒𝑊𝑎𝑡𝑡𝑠))/1000
∆𝑘𝑊=((𝑃𝑟𝑒𝐹𝑖𝑥𝑡𝑢𝑟𝑒𝑄𝑡𝑦 ∗𝑃𝑟𝑒𝐹𝑖𝑥𝑡𝑢𝑟𝑒𝑊𝑎𝑡𝑡𝑠)−(𝑃𝑜𝑠𝑡𝐹𝑖𝑥𝑡𝑢𝑟𝑒𝑄𝑡𝑦 ∗𝑃𝑜𝑠𝑡𝐹𝑖𝑥𝑡𝑢𝑟𝑒𝑊𝑎𝑡𝑡𝑠))/1000∗𝐼𝑆𝑅∗𝑊𝐻𝐹𝑑∗𝐶𝐹
∆𝑘𝑊ℎ=((𝑃𝑟𝑒𝐹𝑖𝑥𝑡𝑢𝑟𝑒𝑄𝑡𝑦∗𝑃𝑟𝑒𝐹𝑖𝑥𝑡𝑢𝑟𝑒𝑊𝑎𝑡𝑡𝑠)−(𝑃𝑜𝑠𝑡𝐹𝑖𝑥𝑡𝑢𝑟𝑒𝑄𝑡𝑦∗𝑃𝑜𝑠𝑡𝐹𝑖𝑥𝑡𝑢𝑟𝑒𝑊𝑎𝑡𝑡𝑠))/1000∗𝐻𝑂𝑈𝑅𝑆∗𝐼𝑆𝑅∗𝑊𝐻𝐹𝑒
∆𝑘𝑊=((𝑃𝑜𝑠𝑡𝐹𝑖𝑥𝑡𝑢𝑟𝑒𝑄𝑡𝑦 ∗𝑃𝑜𝑠𝑡𝐹𝑖𝑥𝑡𝑢𝑟𝑒𝑊𝑎𝑡𝑡𝑠))/1000∗(𝑃𝑜𝑠𝑡𝑆𝑉𝐺𝑑−𝑃𝑟𝑒𝑆𝑉𝐺𝑑)∗𝐼𝑆𝑅∗𝑊𝐻𝐹𝑑∗𝐶𝐹
∆𝑘𝑊ℎ=((𝑃𝑜𝑠𝑡𝐹𝑖𝑥𝑡𝑢𝑟𝑒𝑄𝑡𝑦∗𝑃𝑜𝑠𝑡𝐹𝑖𝑥𝑡𝑢𝑟𝑒𝑊𝑎𝑡𝑡𝑠))/1000∗(𝑃𝑜𝑠𝑡𝑆𝑉𝐺𝑒−𝑃𝑟𝑒𝑆𝑉𝐺𝑒)∗𝐻𝑂𝑈𝑅𝑆∗𝐼𝑆𝑅∗𝑊𝐻𝐹𝑒
∆𝑀𝑀𝐵𝑡𝑢=(〖−∆𝑘𝑊ℎ〗∕𝑊𝐻𝐹𝑒)∗𝐴𝑅∗𝐶∗ 𝐿𝐻𝐹∕𝐸𝑓𝑓

## Project Info & Summary
Version 4.1
Project Info | Savings & Incentive Summary
Contractor: | Estimated SC Peak Demand Savings (kW) | Estimated Annual Energy Savings (kWh) | Estimated Annual Gas Savings (MMBtu) | Estimated Annual Gas Savings (Therms) | Fixture Equipment Cost | Controls Equipment Cost | Equipment Cost ($) | Estimated Incentive ($)
Customer Name:
Customer Contact Name:
Customer Contact Phone:
Customer Contact Email: | 0 | 0 | 0 | 0 | 0 | 0 | 0
Project Site Name:
Project Site Address:
City:
ZIP Code:
Installation Date:*
Electric Rate ($/kWh)
Demand Rate ($/kW)
Total Project Cost:*
Building Type (Select from list):*
***Total Incentive will NOT populate without entering a Total Project Cost

## Prescriptive Rebate Table
Measure Category | Measure | Incentive per Unit | Units | Eligible Pre Fixture Codes | Eligible Post Fixture Codes | Measure Name from Filing | Measure Life (years) | Measure Code | Measure Category | Code
LED Troffer Luminaires | New LED linear recessed troffer for 2x2 and 1x4 luminaires | 75 | Fixture | All_Fixtures | All_Fixtures | LED Fixture Internal | 7 | LEDLT2214 | LED Troffer Luminaires | LED_Troffer_Luminaires
LED Troffer Luminaires | New LED linear recessed troffer for 2x4 luminaires | 100 | Fixture | All_Fixtures | All_Fixtures | LED Fixture Internal | 7 | LEDLT24 | LED Flat Panel Luminaires | LED_Flat_Panel_Luminaires
LED Flat Panel Luminaires | New LED flat panel for 2x2 and 1x4 luminaires | 50 | Fixture | All_Fixtures | All_Fixtures | LED Fixture Internal | 7 | LEDPNL2214 | LED Linear Ambient/Stairwell Luminaires | LED_Linear_Ambient_Stairwell_Luminaires
LED Flat Panel Luminaires | New LED flat panel for 2x4 luminaires | 50 | Fixture | All_Fixtures | All_Fixtures | LED Fixture Internal | 7 | LEDPNL24 | LED Interior Directional Luminaires | LED_Interior_Directional_Luminaires
LED Linear Ambient/Stairwell Luminaires | New LED Linear ambient luminaire with direct and indirect components or Vapor Tight, min. IP65 | 30 | Per Foot | All_Fixtures | All_Fixtures | LED Fixture Internal | 7 | LEDVT | LED Display Case Luminaires | LED_Display_Case_Luminaires
LED Linear Ambient/Stairwell Luminaires | New LED linear ambient luminaire | 30 | Per Foot | All_Fixtures | All_Fixtures | LED Fixture Internal | 7 | LEDLAL | LED High/Low Bay Luminaires | LED_High_Low_Bay_Luminaires
LED Linear Ambient/Stairwell Luminaires | New LED stairwell luminaire | 100 | Fixture | All_Fixtures | All_Fixtures | LED Fixture Internal | 7 | LEDSL | LED Exterior Luminaires | LED_Exterior_Luminaires
LED Interior Directional Luminaires | New LED wall wash luminaire | 30 | Per Foot | All_Fixtures | All_Fixtures | LED Fixture Internal | 7 | LEDWWL | LED Retrofit Kits | LED_Retrofit_Kits
LED Interior Directional Luminaires | New LED track/mono-point luminaire | 40 | Fixture | All_Fixtures | All_Fixtures | LED Fixture Internal | 7 | LEDTMPL | LED ENERGY STAR Fixtures | LED_ENERGY_STAR_Fixtures
LED Display Case Luminaires | New LED display case luminaire | 40 | Fixture | All_Fixtures | All_Fixtures | LED Fixture Internal | 7 | LEDDCL | LED Replacement Lamps | LED_Replacement_Lamps
LED Display Case Luminaires | New LED display case luminaire installed in reach-in coolers/freezers | 50 | Fixture | All_Fixtures | All_Fixtures | LED Reach in Refrigerator / Freezer Lights | 8 | LEDDCLRICF | Exit Signs | Exit_Signs
LED High/Low Bay Luminaires | New LED high/low bay luminaire - DLC reported lumens between 5,000 lm - 9,999 lm | 200 | Fixture | All_Fixtures | All_Fixtures | LED Fixture Internal | 7 | LEDHBLB175 | Linear Fluorescents | Linear_Fluorescents
LED High/Low Bay Luminaires | New LED high/low bay luminaire - DLC reported lumens between 10,000 lm - 19,999 lm | 300 | Fixture | All_Fixtures | All_Fixtures | LED Fixture Internal | 7 | LEDHBLB250 | Street & Area Lighting | Street_and_Area_Lighting
LED High/Low Bay Luminaires | New LED high/low bay luminaire - DLC reported lumens between 20,000 lm - 29,999 lm | 400 | Fixture | All_Fixtures | All_Fixtures | LED Fixture Internal | 7 | LEDHBLB400 | Other | Lighting_Other
LED High/Low Bay Luminaires | New LED high/low bay luminaire - DLC reported lumens between 30,000 lm - 39,999 lm | 500 | Fixture | All_Fixtures | All_Fixtures | LED Fixture Internal | 7 | LEDHBLB1000 | Custom | Lighting_Custom
LED High/Low Bay Luminaires | New LED high/low bay luminaire - DLC reported lumens 40,000 lm or more | 600 | Fixture | All_Fixtures | All_Fixtures | LED Fixture Internal | 7 | LEDHBLB1001 | Networked Lighting Controls | Networked_Lighting_Controls
LED Exterior Luminaires | New LED exterior luminaire - DLC reported lumens 4,999 lm or less | 150 | Fixture | All_Fixtures | All_Fixtures | LED Fixture External | 21 | LEDEL175 | Dual Daylight/Occupancy Controls | Dual_Daylight_Occupancy_Controls
LED Exterior Luminaires | New LED exterior luminaire - DLC reported lumens between 5,000 lm - 9,999 lm | 250 | Fixture | All_Fixtures | All_Fixtures | LED Fixture External | 21 | LEDEL250 | Daylight Controls | Daylight_Controls
LED Exterior Luminaires | New LED exterior luminaire - DLC reported lumens between 10,000 lm - 19,999 lm | 300 | Fixture | All_Fixtures | All_Fixtures | LED Fixture External | 21 | LEDEL400 | Occupancy/Vacancy Controls | Occupancy_Vacancy_Controls
LED Exterior Luminaires | New LED exterior luminaire - DLC reported lumens between 20,000 lm - 29,999 lm | 400 | Fixture | All_Fixtures | All_Fixtures | LED Fixture External | 21 | LEDEL750
LED Exterior Luminaires | New LED exterior luminaire - DLC reported lumens between 30,000 lm - 39,999 lm | 500 | Fixture | All_Fixtures | All_Fixtures | LED Fixture External | 21 | LEDEL1000
LED Exterior Luminaires | New LED exterior luminaire - DLC reported lumens 40,000 lm or more | 600 | Fixture | All_Fixtures | All_Fixtures | LED Fixture External | 21 | LEDEL1001
LED Retrofit Kits | LED linear retrofit kit for 2x2 and 1x4 fixtures | 25 | Fixture | All_Fixtures | All_Fixtures | LED Fixture Internal | 7 | LEDRK2214
LED Retrofit Kits | LED linear retrofit kit for 2x4 fixtures | 45 | Fixture | All_Fixtures | All_Fixtures | LED Fixture Internal | 7 | LEDRK24
LED Retrofit Kits | LED integrated retrofit kit for 2x2 and 1x4 fixtures | 75 | Fixture | All_Fixtures | All_Fixtures | LED Fixture Internal | 7 | LEDIRK2214
LED Retrofit Kits | LED integrated retrofit kit for 2x4 fixtures | 110 | Fixture | All_Fixtures | All_Fixtures | LED Fixture Internal | 7 | LEDIRK24
LED Retrofit Kits | LED integrated flat panel retrofit kit for 2x2 and 1x4 fixtures | 20 | Fixture | All_Fixtures | All_Fixtures | LED Fixture Internal | 7 | LEDPNLRK2214
LED Retrofit Kits | LED integrated flat panel retrofit kit for 2x4 fixtures | 40 | Fixture | All_Fixtures | All_Fixtures | LED Fixture Internal | 7 | LEDPNLRK24
LED Retrofit Kits | LED retrofit kit for linear ambient luminaire | 15 | Per Foot | All_Fixtures | All_Fixtures | LED Fixture Internal | 7 | LEDRKLAL
LED Retrofit Kits | LED retrofit kit for high/low bay luminaire | 100 | Fixture | All_Fixtures | All_Fixtures | LED Fixture Internal | 7 | LEDRKHBLB
LED Retrofit Kits | LED retrofit kit for exterior luminaire | 100 | Fixture | All_Fixtures | All_Fixtures | LED Fixture External | 21 | LEDRKEL
LED ENERGY STAR Fixtures | New LED ENERGY STAR fixture - 1,499 lm or less | 30 | Fixture | All_Fixtures | All_Fixtures | LED Fixture Internal | 7 | ESLED1499
LED ENERGY STAR Fixtures | New LED ENERGY STAR fixture - 1,500 lm - 2,999 lm | 50 | Fixture | All_Fixtures | All_Fixtures | LED Fixture Internal | 7 | ESLED2999
LED ENERGY STAR Fixtures | New LED ENERGY STAR LED fixture - 3,000 lm or greater | 100 | Fixture | All_Fixtures | All_Fixtures | LED Fixture Internal | 7 | ESLED3000
LED Replacement Lamps | LED linear replacement lamp with new LED driver | 10.2 | Lamp | All_Fixtures | All_Fixtures | LED Linear | 14 | LEDLRLND
LED Replacement Lamps | LED linear replacement lamp using internal driver (Type-A) | 6.8 | Lamp | All_Fixtures | All_Fixtures | LED Linear | 14 | LEDLRLTYPEA
LED Replacement Lamps | LED pin-base replacement lamp for CFL | 8.5 | Lamp | All_Fixtures | All_Fixtures | LED Lamps - C&I | 4 | LEDPBRL
LED Replacement Lamps | LED A lamp | 4 | Lamp | All_Fixtures | All_Fixtures | LED Lamps - C&I | 4 | LEDALAMP
LED Replacement Lamps | LED BR/R lamp | 5 | Lamp | All_Fixtures | All_Fixtures | LED Lamps - C&I | 4 | LEDBRRLAMP
LED Replacement Lamps | LED Decorative or Globe lamp | 5 | Lamp | All_Fixtures | All_Fixtures | LED Lamps - C&I | 4 | LEDDGLAMP
LED Replacement Lamps | LED MR lamp | 5 | Lamp | All_Fixtures | All_Fixtures | LED Lamps - C&I | 4 | LEDMRLAMP
LED Replacement Lamps | LED PAR lamp - PAR20 | 5 | Lamp | All_Fixtures | All_Fixtures | LED Lamps - C&I | 4 | LEDPAR20LAMP
LED Replacement Lamps | LED PAR lamp - PAR30 & PAR38 | 10 | Lamp | All_Fixtures | All_Fixtures | LED Lamps - C&I | 4 | LEDPAR3038LAMP
LED Replacement Lamps | LED mogul-screw base replacement for HID lamps and new external driver | 80 | Lamp | All_Fixtures | All_Fixtures | LED Linear | 14 | LEDMSBRL
Exit Signs | LED Exit Sign replacing incandescent or fluorescent | 23 | Fixture | All_Fixtures | All_Fixtures | Exit Signs | 16 | LEDEXIT
Linear Fluorescents | High Performance T8 Lamps or Fixtures replacing standard T8 lamps or fixtures | 15 | Fixture | All_Fixtures | All_Fixtures | Linear Fluorescent | 15 | HPT8
Street & Area Lighting | LED Street & Area Lighting replacing less efficient technology | 200 | Fixture | All_Fixtures | All_Fixtures | Street & Area Lighting (Customer Owned) | 18 | LEDSTREET
Other | Lighting - Other | 0.05 | kWh | All_Fixtures | All_Fixtures | Lighting - Other | 7 | OTHER
Custom | Lighting - Custom | 0.05 | kWh | All_Fixtures | All_Fixtures | Lighting - Custom | 7 | CUSTOM
Networked Lighting Controls | Networked lighting control system controlling efficient luminaires (Min. Watts Controlled = 200) | 0.6 | Per Watt | All_Fixtures | All_Fixtures | Network Lighting Controls | 10 | NLC
Networked Lighting Controls | Networked lighting control w/local or cloud server required | 60 | Fixture | All_Fixtures | All_Fixtures | Network Lighting Controls | 10 | NLCCS150
Networked Lighting Controls | Networked lighting control - w/local or cloud server required - lower wattage fixtures/downlights (Min. Watts Controlled = 20) | 30 | Fixture | All_Fixtures | All_Fixtures | Network Lighting Controls | 10 | NLCCS20
Networked Lighting Controls | Networked lighting control no server required | 50 | Fixture | All_Fixtures | All_Fixtures | Network Lighting Controls | 10 | NLCNS150
Networked Lighting Controls | Networked lighting control no server required - lower wattage fixtures/downlights (Min. Watts Controlled = 20) | 10 | Fixture | All_Fixtures | All_Fixtures | Network Lighting Controls | 10 | NLCNS20
Dual Daylight/Occupancy Controls | Dual daylight & occupancy sensor (DOS) (Min. Watts Controlled = 150) | 50 | Control | All_Fixtures | All_Fixtures | Lighting Controls (Daylight & Occupancy) | 10 | DOS150
Dual Daylight/Occupancy Controls | Dual daylight & occupancy sensor (DOS) - lower wattage fixtures/downlights (Min. Watts Controlled = 20) | 30 | Fixture | All_Fixtures | All_Fixtures | Lighting Controls (Daylight & Occupancy) | 10 | DOS20
Daylight Controls | Daylight continuous dimming control (Min. Watts Controlled = 150) | 40 | Control | All_Fixtures | All_Fixtures | Lighting Controls (Daylight & Occupancy) | 10 | DAYLIGHT150
Daylight Controls | Daylight continuous dimming control - lower wattage fixtures/downlights (Min. Watts Controlled = 20) | 20 | Fixture | All_Fixtures | All_Fixtures | Lighting Controls (Daylight & Occupancy) | 10 | DAYLIGHT20
Occupancy/Vacancy Controls | Vacancy control (Min. Watts Controlled = 150) | 40 | Control | All_Fixtures | All_Fixtures | Lighting Controls (Daylight & Occupancy) | 10 | VACANCY150
Occupancy/Vacancy Controls | Vacancy control - lower wattage fixtures/downlights (Min. Watts Controlled = 20) | 20 | Fixture | All_Fixtures | All_Fixtures | Lighting Controls (Daylight & Occupancy) | 10 | VACANCY20
Occupancy/Vacancy Controls | Occupancy control (Min. Watts Controlled = 150) | 40 | Control | All_Fixtures | All_Fixtures | Lighting Controls (Daylight & Occupancy) | 10 | OCCUPANCY150
Occupancy/Vacancy Controls | Occupancy control - lower wattage fixtures/downlights (Min. Watts Controlled = 20) | 20 | Fixture | All_Fixtures | All_Fixtures | Lighting Controls (Daylight & Occupancy) | 10 | OCCUPANCY20

## Lookups (hidden)
[Building Type] (application premise) | Building Type for Hours & CF | Building Type for WHF | Building Type | Space Type | ConCat | Hours | CFUtility | CFPJM Summer | CFPJM Winter | Buiding Type | HVAC Equipment Type | ConCat | WHFe | WHFd (Utility) | WHFd (PJM Summer) | WHFd (PJM Winter) | Cooling Type | Heating Type | Concat | HVAC Equipment Type | Selected Building Type from App | Measure Category | Measure | Measure Name from Filing | Aspect Ratio | kWh to MMBtu | Fraction contributing to space heating | Heating System Eff. | Heat Type Multiplier
Arena/Auditorium/Convention | Other | Other | Grocery | Auditorium/Gym | GroceryAuditorium/Gym | 3438 | 0.65 | 0.64 | 0.4 | Office | AC/ ElecRes | OfficeAC/ ElecRes | 0.85 | 1.34 | 1.31 | 0.18 | Air Conditioned | Electric Resistance Heating | Air ConditionedElectric Resistance Heating | AC/ ElecRes |  | LED Troffer Luminaires | New LED linear recessed troffer for 2x2 and 1x4 luminaires | LED Fixture Internal | 0.7 | 0.003413 | 0.23 | 0.75 | 1
Auto-Related | Retail | Retail | Grocery | Auto Repair Workshop | GroceryAuto Repair Workshop | 6189 | 0.88 | 0.89 | 0.61 | Office | AC/ NonElec | OfficeAC/ NonElec | 1.1 | 1.34 | 1.31 | 1 | Air Conditioned | Gas | Air ConditionedGas | AC/ NonElec |  | LED Troffer Luminaires | New LED linear recessed troffer for 2x4 luminaires | LED Fixture Internal | 0.7 | 0.003413 | 0.23 | 0.75 | 1
Convenience Stores | Retail | Retail | Grocery | Bank/Financial | GroceryBank/Financial | 3438 | 0.65 | 0.64 | 0.4 | Office | AC/ Unconditioned | OfficeAC/ Unconditioned | 1 | 1.34 | 1.31 | 1 | Air Conditioned | Unconditioned | Air ConditionedUnconditioned | AC/ Unconditioned |  | LED Flat Panel Luminaires | New LED flat panel for 2x2 and 1x4 luminaires | LED Fixture Internal | 0.7 | 0.003413 | 0.23 | 0.75 | 1
Daycare | School | School | Grocery | Bar Cocktail Lounge | GroceryBar Cocktail Lounge | 3438 | 0.65 | 0.64 | 0.4 | Office | AC/ Unknown | OfficeAC/ Unknown | 1 | 1.34 | 1.31 | 0.68 | Air Conditioned | Unknown | Air ConditionedUnknown | AC/ Unknown |  | LED Flat Panel Luminaires | New LED flat panel for 2x4 luminaires | LED Fixture Internal | 0.7 | 0.003413 | 0.23 | 0.75 | 1
Education - College/University | School | School | Grocery | Barber/Beauty Shop | GroceryBarber/Beauty Shop | 3438 | 0.65 | 0.64 | 0.4 | Office | Heat Pump | OfficeHeat Pump | 0.94 | 1.34 | 1.31 | 0.6 | Air Conditioned w/ Heat Pump | Heated w/ Heat Pump | Air Conditioned w/ Heat PumpHeated w/ Heat Pump | Heat Pump |  | LED Linear Ambient/Stairwell Luminaires | New LED Linear ambient luminaire with direct and indirect components or Vapor Tight, min. IP65 | LED Fixture Internal | 0.7 | 0.003413 | 0.23 | 0.75 | 1
Education - K-12 | School | School | Grocery | Casino/Gaming | GroceryCasino/Gaming | 3438 | 0.65 | 0.64 | 0.4 | Office | Heat Pump/ Unconditioned | OfficeHeat Pump/ Unconditioned | 1 | 1.34 | 1.31 | 1 | Air Conditioned w/ Heat Pump | Unconditioned | Air Conditioned w/ Heat PumpUnconditioned | Heat Pump/ Unconditioned |  | LED Linear Ambient/Stairwell Luminaires | New LED linear ambient luminaire | LED Fixture Internal | 0.7 | 0.003413 | 0.23 | 0.75 | 1
Grocery | Grocery | Other | Grocery | Classroom/Lecture | GroceryClassroom/Lecture | 1584 | 0.24 | 0.24 | 0.2 | Office | Heat Pump/ Unknown | OfficeHeat Pump/ Unknown | 1 | 1.34 | 1.31 | 0.68 | Air Conditioned w/ Heat Pump | Unknown | Air Conditioned w/ Heat PumpUnknown | Heat Pump/ Unknown |  | LED Linear Ambient/Stairwell Luminaires | New LED stairwell luminaire | LED Fixture Internal | 0.7 | 0.003413 | 0.23 | 0.75 | 1
Gymnasium/Performing Arts Theater | Other | Other | Grocery | Clean Room | GroceryClean Room | 3438 | 0.65 | 0.64 | 0.4 | Office | NoAC/ ElecRes | OfficeNoAC/ ElecRes | 0.75 | 1 | 1 | 0.18 | Refrigerated | Unconditioned | RefrigeratedUnconditioned | Refrigerated/ Unconditioned |  | LED Interior Directional Luminaires | New LED wall wash luminaire | LED Fixture Internal | 0.7 | 0.003413 | 0.23 | 0.75 | 1
Industrial - 1 Shift | Warehouse_Industrial | Warehouse | Grocery | Computer Room/Data Processing | GroceryComputer Room/Data Processing | 3438 | 0.65 | 0.64 | 0.4 | Office | NoAC/ NonElec | OfficeNoAC/ NonElec | 1 | 1 | 1 | 1 | Freezer | Unconditioned | FreezerUnconditioned | Freezer/ Unconditioned |  | LED Interior Directional Luminaires | New LED track/mono-point luminaire | LED Fixture Internal | 0.7 | 0.003413 | 0.23 | 0.75 | 1
Industrial - 2 Shift | Warehouse_Industrial | Warehouse | Grocery | Comm/Ind Work(General High Bay flr-to-clng ht >= 25ft) | GroceryComm/Ind Work(General High Bay flr-to-clng ht >= 25ft) | 4790 | 0.9 | 0.91 | 0.82 | Office | NoAC/ Unconditioned | OfficeNoAC/ Unconditioned | 1 | 1 | 1 | 1 | Not Air Conditioned | Electric Resistance Heating | Not Air ConditionedElectric Resistance Heating | NoAC/ ElecRes |  | LED Display Case Luminaires | New LED display case luminaire | LED Fixture Internal | 0.7 | 0.003413 | 0.23 | 0.75 | 1
Industrial - 3 Shift | Warehouse_Industrial | Warehouse | Grocery | Comm/Ind Work(General Low Bay flr-to-clng ht < 25ft) | GroceryComm/Ind Work(General Low Bay flr-to-clng ht < 25ft) | 6775 | 0.95 | 0.95 | 0.77 | Office | NoAC/ Unknown | OfficeNoAC/ Unknown | 1 | 1 | 1 | 0.68 | Not Air Conditioned | Gas | Not Air ConditionedGas | NoAC/ NonElec |  | LED Display Case Luminaires | New LED display case luminaire installed in reach-in coolers/freezers | LED Reach in Refrigerator / Freezer Lights | 0 | 0 | 0 | 0 | 0
Lodging - Common Areas | Other | Other | Grocery | Comm/Ind Work (Precision) | GroceryComm/Ind Work (Precision) | 3438 | 0.65 | 0.64 | 0.4 | Office | Unknown/ ElecRes | OfficeUnknown/ ElecRes | 1 | 1 | 1 | 0.18 | Not Air Conditioned | Unconditioned | Not Air ConditionedUnconditioned | NoAC/ Unconditioned |  | LED High/Low Bay Luminaires | New LED high/low bay luminaire - DLC reported lumens between 5,000 lm - 9,999 lm | LED Fixture Internal | 1 | 0.003413 | 0.23 | 0.75 | 1
Lodging (MF - Dorms) | Other | Other | Grocery | Conference Room | GroceryConference Room | 1201 | 0.28 | 0.3 | 0.16 | Office | Unknown/ NonElec | OfficeUnknown/ NonElec | 1 | 1 | 1 | 1 | Not Air Conditioned | Unknown | Not Air ConditionedUnknown | NoAC/ Unknown |  | LED High/Low Bay Luminaires | New LED high/low bay luminaire - DLC reported lumens between 10,000 lm - 19,999 lm | LED Fixture Internal | 1 | 0.003413 | 0.23 | 0.75 | 1
Lodging Hotel (Guest Rooms) | Other | Other | Grocery | Convention and Meeting Center | GroceryConvention and Meeting Center | 3438 | 0.65 | 0.64 | 0.4 | Office | Unknown/ Unconditioned | OfficeUnknown/ Unconditioned | 1 | 1 | 1 | 1 | Unknown | Electric Resistance Heating | UnknownElectric Resistance Heating | Unknown/ ElecRes |  | LED High/Low Bay Luminaires | New LED high/low bay luminaire - DLC reported lumens between 20,000 lm - 29,999 lm | LED Fixture Internal | 1 | 0.003413 | 0.23 | 0.75 | 1
Medical - Clinic | Health | Other | Grocery | Copy Room | GroceryCopy Room | 3438 | 0.65 | 0.64 | 0.4 | Office | Unknown/ Unknown | OfficeUnknown/ Unknown | 1 | 1 | 1 | 0.68 | Unknown | Gas | UnknownGas | Unknown/ NonElec |  | LED High/Low Bay Luminaires | New LED high/low bay luminaire - DLC reported lumens between 30,000 lm - 39,999 lm | LED Fixture Internal | 1 | 0.003413 | 0.23 | 0.75 | 1
Medical - Hospital | Health | Other | Grocery | Corridor/Hallways | GroceryCorridor/Hallways | 5670 | 0.86 | 0.86 | 0.73 | Office | Refrigerated/ Unconditioned | OfficeRefrigerated/ Unconditioned | 1.41 | 1.4 | 1.4 | 1.4 | Unknown | Unconditioned | UnknownUnconditioned | Unknown/ Unconditioned |  | LED High/Low Bay Luminaires | New LED high/low bay luminaire - DLC reported lumens 40,000 lm or more | LED Fixture Internal | 1 | 0.003413 | 0.23 | 0.75 | 1
Multi-Family (Common Areas) | Other | Other | Grocery | Courtrooms | GroceryCourtrooms | 3438 | 0.65 | 0.64 | 0.4 | Office | Freezer/ Unconditioned | OfficeFreezer/ Unconditioned | 1.52 | 1.51 | 1.51 | 1.51 | Unknown | Unknown | UnknownUnknown | Unknown/ Unknown |  | LED Exterior Luminaires | New LED exterior luminaire - DLC reported lumens 4,999 lm or less | LED Fixture External | 0 | 0 | 0 | 0 | 0
Museum/Library | Office | Office | Grocery | Dining Area | GroceryDining Area | 2962 | 0.48 | 0.53 | 0.51 | Retail | AC/ ElecRes | RetailAC/ ElecRes | 0.83 | 1.27 | 1.25 | 0.41 | [5 empty] | LED Exterior Luminaires | New LED exterior luminaire - DLC reported lumens between 5,000 lm - 9,999 lm | LED Fixture External | 0 | 0 | 0 | 0 | 0
Nursing Homes | Health | Other | Grocery | Dry Cleaning | GroceryDry Cleaning | 3438 | 0.65 | 0.64 | 0.4 | Retail | AC/ NonElec | RetailAC/ NonElec | 1.06 | 1.27 | 1.25 | 1 | Cooling Type | Code |  |  |  | LED Exterior Luminaires | New LED exterior luminaire - DLC reported lumens between 10,000 lm - 19,999 lm | LED Fixture External | 0 | 0 | 0 | 0 | 0
Office | Office | Office | Grocery | Exercise Centers/Gymnasium | GroceryExercise Centers/Gymnasium | 4833 | 0.81 | 0.82 | 0.6 | Retail | AC/ Unconditioned | RetailAC/ Unconditioned | 1 | 1.27 | 1.25 | 1 | Air Conditioned | AC |  |  |  | LED Exterior Luminaires | New LED exterior luminaire - DLC reported lumens between 20,000 lm - 29,999 lm | LED Fixture External | 0 | 0 | 0 | 0 | 0
Other | Other | Other | Grocery | Exhibit Display Area/Museum | GroceryExhibit Display Area/Museum | 3438 | 0.65 | 0.64 | 0.4 | Retail | AC/ Unknown | RetailAC/ Unknown | 1 | 1.27 | 1.25 | 0.83 | Air Conditioned w/ Heat Pump | HP |  |  |  | LED Exterior Luminaires | New LED exterior luminaire - DLC reported lumens between 30,000 lm - 39,999 lm | LED Fixture External | 0 | 0 | 0 | 0 | 0
Penitentiary | Other | Other | Grocery | Guest Room (Hotel/Motel) | GroceryGuest Room (Hotel/Motel) | 3438 | 0.65 | 0.64 | 0.4 | Retail | Heat Pump | RetailHeat Pump | 0.95 | 1.27 | 1.25 | 0.71 | Refrigerated | Refrigerated |  |  |  | LED Exterior Luminaires | New LED exterior luminaire - DLC reported lumens 40,000 lm or more | LED Fixture External | 0 | 0 | 0 | 0 | 0
Police/Fire Stations | Other | Other | Grocery | Kitchen/Break room & Food Prep | GroceryKitchen/Break room & Food Prep | 3522 | 0.79 | 0.74 | 0.42 | Retail | Heat Pump/ Unconditioned | RetailHeat Pump/ Unconditioned | 1 | 1.27 | 1.25 | 1 | Freezer | Freezer |  |  |  | LED Retrofit Kits | LED linear retrofit kit for 2x2 and 1x4 fixtures | LED Fixture Internal | 0.7 | 0.003413 | 0.23 | 0.75 | 1
Post Office/Town Hall/Court | Office | Office | Grocery | Laboratory | GroceryLaboratory | 3438 | 0.65 | 0.64 | 0.4 | Retail | Heat Pump/ Unknown | RetailHeat Pump/ Unknown | 1 | 1.27 | 1.25 | 0.83 | Not Air Conditioned | None |  |  |  | LED Retrofit Kits | LED linear retrofit kit for 2x4 fixtures | LED Fixture Internal | 0.7 | 0.003413 | 0.23 | 0.75 | 1
Public Assembly | Other | Other | Grocery | Laundry | GroceryLaundry | 3438 | 0.65 | 0.64 | 0.4 | Retail | NoAC/ ElecRes | RetailNoAC/ ElecRes | 0.77 | 1 | 1 | 0.41 | Unknown | Unknown |  |  |  | LED Retrofit Kits | LED integrated retrofit kit for 2x2 and 1x4 fixtures | LED Fixture Internal | 0.7 | 0.003413 | 0.23 | 0.75 | 1
Public Order/Safety | Other | Other | Grocery | Library | GroceryLibrary | 1957 | 0.44 | 0.46 | 0.31 | Retail | NoAC/ NonElec | RetailNoAC/ NonElec | 1 | 1 | 1 | 1 | [5 empty] | LED Retrofit Kits | LED integrated retrofit kit for 2x4 fixtures | LED Fixture Internal | 0.7 | 0.003413 | 0.23 | 0.75 | 1
Public Services (Non-food) | Office | Office | Grocery | Loading Dock | GroceryLoading Dock | 7358 | 0.97 | 0.97 | 0.62 | Retail | NoAC/ Unconditioned | RetailNoAC/ Unconditioned | 1 | 1 | 1 | 1 | [5 empty] | LED Retrofit Kits | LED integrated flat panel retrofit kit for 2x2 and 1x4 fixtures | LED Fixture Internal | 0.7 | 0.003413 | 0.23 | 0.75 | 1
Religious Worship/Church | Other | Other | Grocery | Lobby (Hotel) | GroceryLobby (Hotel) | 3438 | 0.65 | 0.64 | 0.4 | Retail | NoAC/ Unknown | RetailNoAC/ Unknown | 1 | 1 | 1 | 0.83 | [5 empty] | LED Retrofit Kits | LED integrated flat panel retrofit kit for 2x4 fixtures | LED Fixture Internal | 0.7 | 0.003413 | 0.23 | 0.75 | 1
Restaurant - Fast-Food | Retail | Retail | Grocery | Lobby (Main Entry and Assembly) | GroceryLobby (Main Entry and Assembly) | 5947 | 0.83 | 0.82 | 0.71 | Retail | Unknown/ ElecRes | RetailUnknown/ ElecRes | 1 | 1 | 1 | 0.41 | [5 empty] | LED Retrofit Kits | LED retrofit kit for linear ambient luminaire | LED Fixture Internal | 0.7 | 0.003413 | 0.23 | 0.75 | 1
Restaurant - Sit-Down | Retail | Retail | Grocery | Lobby (Office Reception/Waiting) | GroceryLobby (Office Reception/Waiting) | 3425 | 0.84 | 0.87 | 0.49 | Retail | Unknown/ NonElec | RetailUnknown/ NonElec | 1 | 1 | 1 | 1 | [5 empty] | LED Retrofit Kits | LED retrofit kit for high/low bay luminaire | LED Fixture Internal | 0.7 | 0.003413 | 0.23 | 0.75 | 1
Retail - Large | Retail | Retail | Grocery | Locker and Dressing Room | GroceryLocker and Dressing Room | 3438 | 0.65 | 0.64 | 0.4 | Retail | Unknown/ Unconditioned | RetailUnknown/ Unconditioned | 1 | 1 | 1 | 1 | [5 empty] | LED Retrofit Kits | LED retrofit kit for exterior luminaire | LED Fixture External | 0 | 0 | 0 | 0 | 0
Retail - Small | Retail | Retail | Grocery | Mall Arcade and Atrium | GroceryMall Arcade and Atrium | 3438 | 0.65 | 0.64 | 0.4 | Retail | Unknown/ Unknown | RetailUnknown/ Unknown | 1 | 1 | 1 | 0.83 | [5 empty] | LED ENERGY STAR Fixtures | New LED ENERGY STAR fixture - 1,499 lm or less | LED Fixture Internal | 0.7 | 0.003413 | 0.23 | 0.75 | 1
Storage - Conditioned | Other | Other | Grocery | Mechanical/Electrical Room | GroceryMechanical/Electrical Room | 5026 | 0.73 | 0.74 | 0.46 | Retail | Refrigerated/ Unconditioned | RetailRefrigerated/ Unconditioned | 1.41 | 1.4 | 1.4 | 1.4 | [5 empty] | LED ENERGY STAR Fixtures | New LED ENERGY STAR fixture - 1,500 lm - 2,999 lm | LED Fixture Internal | 0.7 | 0.003413 | 0.23 | 0.75 | 1
Storage - Unconditioned | Other | Other | Grocery | Medical Offices and Exam rooms | GroceryMedical Offices and Exam rooms | 3438 | 0.65 | 0.64 | 0.4 | Retail | Freezer/ Unconditioned | RetailFreezer/ Unconditioned | 1.52 | 1.51 | 1.51 | 1.51 | [5 empty] | LED ENERGY STAR Fixtures | New LED ENERGY STAR LED fixture - 3,000 lm or greater | LED Fixture Internal | 0.7 | 0.003413 | 0.23 | 0.75 | 1
Warehouse - Non-Refrigerated | Warehouse_Industrial | Warehouse | Grocery | Office (Executive/Private) | GroceryOffice (Executive/Private) | 1753 | 0.42 | 0.44 | 0.2 | School | AC/ ElecRes | SchoolAC/ ElecRes | 0.81 | 1.45 | 1.45 | 0.16 | [5 empty] | LED Replacement Lamps | LED linear replacement lamp with new LED driver | LED Linear | 0.7 | 0.003413 | 0.23 | 0.75 | 1
Warehouse - Refrigerated | Warehouse_Industrial | Warehouse | Grocery | Office (General) | GroceryOffice (General) | 3001 | 0.67 | 0.67 | 0.43 | School | AC/ NonElec | SchoolAC/ NonElec | 1.1 | 1.45 | 1.45 | 1 | [5 empty] | LED Replacement Lamps | LED linear replacement lamp using internal driver (Type-A) | LED Linear | 0.7 | 0.003413 | 0.23 | 0.75 | 1
Waste Water Treatment Plant | Other | Other | Grocery | Office(Open Plan) | GroceryOffice(Open Plan) | 3159 | 0.81 | 0.82 | 0.49 | School | AC/ Unconditioned | SchoolAC/ Unconditioned | 1 | 1.45 | 1.45 | 1 | [5 empty] | LED Replacement Lamps | LED pin-base replacement lamp for CFL | LED Lamps - C&I | 0.7 | 0.003413 | 0.23 | 0.75 | 1
|  |  | Grocery | Patient Rooms | GroceryPatient Rooms | 3438 | 0.65 | 0.64 | 0.4 | School | AC/ Unknown | SchoolAC/ Unknown | 1 | 1.45 | 1.45 | 0.93 | [5 empty] | LED Replacement Lamps | LED A lamp | LED Lamps - C&I | 0.7 | 0.003413 | 0.23 | 0.75 | 1
|  |  | Grocery | Patio Area | GroceryPatio Area | 3438 | 0.65 | 0.64 | 0.4 | School | Heat Pump | SchoolHeat Pump | 0.96 | 1.45 | 1.45 | 0.59 | [5 empty] | LED Replacement Lamps | LED BR/R lamp | LED Lamps - C&I | 0.7 | 0.003413 | 0.23 | 0.75 | 1
Control Type | SVGe | SVGd | Grocery | Pool/Spa Area | GroceryPool/Spa Area | 3438 | 0.65 | 0.64 | 0.4 | School | Heat Pump/ Unconditioned | SchoolHeat Pump/ Unconditioned | 1 | 1.45 | 1.45 | 1 | [5 empty] | LED Replacement Lamps | LED Decorative or Globe lamp | LED Lamps - C&I | 0.7 | 0.003413 | 0.23 | 0.75 | 1
None | 0 | 0 | Grocery | Police/Fire Station | GroceryPolice/Fire Station | 3438 | 0.65 | 0.64 | 0.4 | School | Heat Pump/ Unknown | SchoolHeat Pump/ Unknown | 1 | 1.45 | 1.45 | 0.93 | [5 empty] | LED Replacement Lamps | LED MR lamp | LED Lamps - C&I | 0.7 | 0.003413 | 0.23 | 0.75 | 1
Networked lighting control system controlling efficient luminaires (Min. Watts Controlled = 200) | 0.47 | 0.47 | Grocery | Religious Worship | GroceryReligious Worship | 3438 | 0.65 | 0.64 | 0.4 | School | NoAC/ ElecRes | SchoolNoAC/ ElecRes | 0.71 | 1 | 1 | 0.16 | [5 empty] | LED Replacement Lamps | LED PAR lamp - PAR20 | LED Lamps - C&I | 0.7 | 0.003413 | 0.23 | 0.75 | 1
Networked lighting control w/local or cloud server required | 0.47 | 0.47 | Grocery | Residential | GroceryResidential | 3438 | 0.65 | 0.64 | 0.4 | School | NoAC/ NonElec | SchoolNoAC/ NonElec | 1 | 1 | 1 | 1 | [5 empty] | LED Replacement Lamps | LED PAR lamp - PAR30 & PAR38 | LED Lamps - C&I | 0.7 | 0.003413 | 0.23 | 0.75 | 1
Networked lighting control - w/local or cloud server required - lower wattage fixtures/downlights (Min. Watts Controlled = 20) | 0.47 | 0.47 | Grocery | Restrooms | GroceryRestrooms | 2521 | 0.48 | 0.42 | 0.3 | School | NoAC/ Unconditioned | SchoolNoAC/ Unconditioned | 1 | 1 | 1 | 1 | [5 empty] | LED Replacement Lamps | LED mogul-screw base replacement for HID lamps and new external driver | LED Linear | 1 | 0.003413 | 0.23 | 0.75 | 1
Networked lighting control no server required | 0.47 | 0.47 | Grocery | Retail Sales/Showroom | GroceryRetail Sales/Showroom | 7374 | 0.98 | 0.98 | 0.93 | School | NoAC/ Unknown | SchoolNoAC/ Unknown | 1 | 1 | 1 | 0.93 | [5 empty] | Exit Signs | LED Exit Sign replacing incandescent or fluorescent | Exit Signs | 0.7 | 0.003413 | 0.23 | 0.75 | 1
Networked lighting control no server required - lower wattage fixtures/downlights (Min. Watts Controlled = 20) | 0.47 | 0.47 | Grocery | Smoking Lounge | GrocerySmoking Lounge | 3438 | 0.65 | 0.64 | 0.4 | School | Unknown/ ElecRes | SchoolUnknown/ ElecRes | 1 | 1 | 1 | 0.16 | [5 empty] | Linear Fluorescents | High Performance T8 Lamps or Fixtures replacing standard T8 lamps or fixtures | Linear Fluorescent | 0.7 | 0.003413 | 0.23 | 0.75 | 0.224
Dual daylight & occupancy sensor (DOS) (Min. Watts Controlled = 150) | 0.38 | 0.38 | Grocery | Storage (Conditioned) | GroceryStorage (Conditioned) | 6027 | 0.84 | 0.84 | 0.82 | School | Unknown/ NonElec | SchoolUnknown/ NonElec | 1 | 1 | 1 | 1 | [5 empty] | Street & Area Lighting | LED Street & Area Lighting replacing less efficient technology | Street & Area Lighting (Customer Owned) | 0 | 0 | 0 | 0 | 0
Dual daylight & occupancy sensor (DOS) - lower wattage fixtures/downlights (Min. Watts Controlled = 20) | 0.38 | 0.38 | Grocery | Storage (Unconditioned) | GroceryStorage (Unconditioned) | 2930 | 0.66 | 0.64 | 0.4 | School | Unknown/ Unconditioned | SchoolUnknown/ Unconditioned | 1 | 1 | 1 | 1 | [5 empty] | Other | Lighting - Other | Lighting - Other | 0.7 | 0.003413 | 0.23 | 0.75 | 1
Daylight continuous dimming control (Min. Watts Controlled = 150) | 0.28 | 0.28 | Grocery | Storage (Refrigerated/Freezer),Walk-in | GroceryStorage (Refrigerated/Freezer),Walk-in | 5851 | 1 | 0.99 | 0.98 | School | Unknown/ Unknown | SchoolUnknown/ Unknown | 1 | 1 | 1 | 0.93 | [5 empty] | Custom | Lighting - Custom | Lighting - Custom | 0.7 | 0.003413 | 0.23 | 0.75 | 1
Daylight continuous dimming control - lower wattage fixtures/downlights (Min. Watts Controlled = 20) | 0.28 | 0.28 | Grocery | Storage (Refrigerated/Freezer),Building | GroceryStorage (Refrigerated/Freezer),Building | 3438 | 0.65 | 0.64 | 0.4 | School | Refrigerated/ Unconditioned | SchoolRefrigerated/ Unconditioned | 1.41 | 1.4 | 1.4 | 1.4 | [5 empty] | Networked Lighting Controls | Networked lighting control system controlling efficient luminaires (Min. Watts Controlled = 200) | Network Lighting Controls | 1 | 0.003413 | 0.23 | 0.75 | 1
Vacancy control (Min. Watts Controlled = 150) | 0.28 | 0.14 | Grocery | Surgery Rooms | GrocerySurgery Rooms | 3438 | 0.65 | 0.64 | 0.4 | School | Freezer/ Unconditioned | SchoolFreezer/ Unconditioned | 1.52 | 1.51 | 1.51 | 1.51 | [5 empty] | Networked Lighting Controls | Networked lighting control w/local or cloud server required | Network Lighting Controls | 1 | 0.003413 | 0.23 | 0.75 | 1
Vacancy control - lower wattage fixtures/downlights (Min. Watts Controlled = 20) | 0.28 | 0.14 | Grocery | Theater (Motion Picture) | GroceryTheater (Motion Picture) | 3438 | 0.65 | 0.64 | 0.4 | Warehouse | AC/ ElecRes | WarehouseAC/ ElecRes | 0.75 | 1.2 | 1.21 | 0.23 | [5 empty] | Networked Lighting Controls | Networked lighting control - w/local or cloud server required - lower wattage fixtures/downlights (Min. Watts Controlled = 20) | Network Lighting Controls | 1 | 0.003413 | 0.23 | 0.75 | 1
Occupancy control (Min. Watts Controlled = 150) | 0.28 | 0.14 | Grocery | Theater (Performance) | GroceryTheater (Performance) | 3438 | 0.65 | 0.64 | 0.4 | Warehouse | AC/ NonElec | WarehouseAC/ NonElec | 1.02 | 1.2 | 1.21 | 1 | [5 empty] | Networked Lighting Controls | Networked lighting control no server required | Network Lighting Controls | 1 | 0.003413 | 0.23 | 0.75 | 1
Occupancy control - lower wattage fixtures/downlights (Min. Watts Controlled = 20) | 0.28 | 0.14 | Grocery | Unknown | GroceryUnknown | 3438 | 0.65 | 0.64 | 0.4 | Warehouse | AC/ Unconditioned | WarehouseAC/ Unconditioned | 1 | 1.2 | 1.21 | 1 | [5 empty] | Networked Lighting Controls | Networked lighting control no server required - lower wattage fixtures/downlights (Min. Watts Controlled = 20) | Network Lighting Controls | 1 | 0.003413 | 0.23 | 0.75 | 1
|  |  | Grocery | Vacant (Condtioned) | GroceryVacant (Condtioned) | 3438 | 0.65 | 0.64 | 0.4 | Warehouse | AC/ Unknown | WarehouseAC/ Unknown | 1 | 1.2 | 1.21 | 0.91 | [5 empty] | Dual Daylight/Occupancy Controls | Dual daylight & occupancy sensor (DOS) (Min. Watts Controlled = 150) | Lighting Controls (Daylight & Occupancy) | 0.7 | 0.003413 | 0.23 | 0.75 | 1
|  |  | Grocery | Vacant (Unconditioned) | GroceryVacant (Unconditioned) | 3438 | 0.65 | 0.64 | 0.4 | Warehouse | Heat Pump | WarehouseHeat Pump | 0.89 | 1.2 | 1.21 | 0.62 | [5 empty] | Dual Daylight/Occupancy Controls | Dual daylight & occupancy sensor (DOS) - lower wattage fixtures/downlights (Min. Watts Controlled = 20) | Lighting Controls (Daylight & Occupancy) | 0.7 | 0.003413 | 0.23 | 0.75 | 1
Control Type Code Mapping |  |  | Grocery | Vocational Areas | GroceryVocational Areas | 3438 | 0.65 | 0.64 | 0.4 | Warehouse | Heat Pump/ Unconditioned | WarehouseHeat Pump/ Unconditioned | 1 | 1.2 | 1.21 | 1 | [5 empty] | Daylight Controls | Daylight continuous dimming control (Min. Watts Controlled = 150) | Lighting Controls (Daylight & Occupancy) | 0.7 | 0.003413 | 0.23 | 0.75 | 1
Control Type | Code |  | Grocery | Parking Garage | GroceryParking Garage | 8678 | 0.98 | 0.98 | 0.99 | Warehouse | Heat Pump/ Unknown | WarehouseHeat Pump/ Unknown | 1 | 1.2 | 1.21 | 0.91 | [5 empty] | Daylight Controls | Daylight continuous dimming control - lower wattage fixtures/downlights (Min. Watts Controlled = 20) | Lighting Controls (Daylight & Occupancy) | 0.7 | 0.003413 | 0.23 | 0.75 | 1
None | NONE |  | Grocery | Non Rebated Area | GroceryNon Rebated Area | 3438 | 0.65 | 0.64 | 0.4 | Warehouse | NoAC/ ElecRes | WarehouseNoAC/ ElecRes | 0.73 | 1 | 1 | 0.23 | [5 empty] | Occupancy/Vacancy Controls | Vacancy control (Min. Watts Controlled = 150) | Lighting Controls (Daylight & Occupancy) | 0.7 | 0.003413 | 0.23 | 0.75 | 1
Networked lighting control system controlling efficient luminaires (Min. Watts Controlled = 200) | NLC |  | Grocery | Other Unlisted Activity Types | GroceryOther Unlisted Activity Types | 6027 | 0.84 | 0.84 | 0.82 | Warehouse | NoAC/ NonElec | WarehouseNoAC/ NonElec | 1 | 1 | 1 | 1 | [5 empty] | Occupancy/Vacancy Controls | Vacancy control - lower wattage fixtures/downlights (Min. Watts Controlled = 20) | Lighting Controls (Daylight & Occupancy) | 0.7 | 0.003413 | 0.23 | 0.75 | 1
Networked lighting control w/local or cloud server required | NLCCS150 |  | Grocery | Outside/Outdoor Area | GroceryOutside/Outdoor Area | 3604 | 0.11 | 0.11 | 0.58 | Warehouse | NoAC/ Unconditioned | WarehouseNoAC/ Unconditioned | 1 | 1 | 1 | 1 | [5 empty] | Occupancy/Vacancy Controls | Occupancy control (Min. Watts Controlled = 150) | Lighting Controls (Daylight & Occupancy) | 0.7 | 0.003413 | 0.23 | 0.75 | 1
Networked lighting control - w/local or cloud server required - lower wattage fixtures/downlights (Min. Watts Controlled = 20) | NLCCS20 |  | Health | Auditorium/Gym | HealthAuditorium/Gym | 3438 | 0.65 | 0.64 | 0.4 | Warehouse | NoAC/ Unknown | WarehouseNoAC/ Unknown | 1 | 1 | 1 | 0.91 | [5 empty] | Occupancy/Vacancy Controls | Occupancy control - lower wattage fixtures/downlights (Min. Watts Controlled = 20) | Lighting Controls (Daylight & Occupancy) | 0.7 | 0.003413 | 0.23 | 0.75 | 1
Networked lighting control no server required | NLCNS150 |  | Health | Auto Repair Workshop | HealthAuto Repair Workshop | 6189 | 0.88 | 0.89 | 0.61 | Warehouse | Unknown/ ElecRes | WarehouseUnknown/ ElecRes | 1 | 1 | 1 | 0.23
Networked lighting control no server required - lower wattage fixtures/downlights (Min. Watts Controlled = 20) | NLCNS20 |  | Health | Bank/Financial | HealthBank/Financial | 3438 | 0.65 | 0.64 | 0.4 | Warehouse | Unknown/ NonElec | WarehouseUnknown/ NonElec | 1 | 1 | 1 | 1
Dual daylight & occupancy sensor (DOS) (Min. Watts Controlled = 150) | DOS150 |  | Health | Bar Cocktail Lounge | HealthBar Cocktail Lounge | 3438 | 0.65 | 0.64 | 0.4 | Warehouse | Unknown/ Unconditioned | WarehouseUnknown/ Unconditioned | 1 | 1 | 1 | 1
Dual daylight & occupancy sensor (DOS) - lower wattage fixtures/downlights (Min. Watts Controlled = 20) | DOS20 |  | Health | Barber/Beauty Shop | HealthBarber/Beauty Shop | 3438 | 0.65 | 0.64 | 0.4 | Warehouse | Unknown/ Unknown | WarehouseUnknown/ Unknown | 1 | 1 | 1 | 0.91
Daylight continuous dimming control (Min. Watts Controlled = 150) | DAYLIGHT150 |  | Health | Casino/Gaming | HealthCasino/Gaming | 3438 | 0.65 | 0.64 | 0.4 | Warehouse | Refrigerated/ Unconditioned | WarehouseRefrigerated/ Unconditioned | 1.41 | 1.4 | 1.4 | 1.4
Daylight continuous dimming control - lower wattage fixtures/downlights (Min. Watts Controlled = 20) | DAYLIGHT20 |  | Health | Classroom/Lecture | HealthClassroom/Lecture | 1584 | 0.24 | 0.24 | 0.2 | Warehouse | Freezer/ Unconditioned | WarehouseFreezer/ Unconditioned | 1.52 | 1.51 | 1.51 | 1.51
Vacancy control (Min. Watts Controlled = 150) | VACANCY150 |  | Health | Clean Room | HealthClean Room | 3438 | 0.65 | 0.64 | 0.4 | Other | AC/ ElecRes | OtherAC/ ElecRes | 0.82 | 1.33 | 1.31 | 0.2
Vacancy control - lower wattage fixtures/downlights (Min. Watts Controlled = 20) | VACANCY20 |  | Health | Computer Room/Data Processing | HealthComputer Room/Data Processing | 3438 | 0.65 | 0.64 | 0.4 | Other | AC/ NonElec | OtherAC/ NonElec | 1.08 | 1.33 | 1.31 | 1
Occupancy control (Min. Watts Controlled = 150) | OCCUPANCY150 |  | Health | Comm/Ind Work(General High Bay flr-to-clng ht >= 25ft) | HealthComm/Ind Work(General High Bay flr-to-clng ht >= 25ft) | 4790 | 0.9 | 0.91 | 0.82 | Other | AC/ Unconditioned | OtherAC/ Unconditioned | 1 | 1.33 | 1.31 | 1
Occupancy control - lower wattage fixtures/downlights (Min. Watts Controlled = 20) | OCCUPANCY20 |  | Health | Comm/Ind Work(General Low Bay flr-to-clng ht < 25ft) | HealthComm/Ind Work(General Low Bay flr-to-clng ht < 25ft) | 6775 | 0.95 | 0.95 | 0.77 | Other | AC/ Unknown | OtherAC/ Unknown | 1 | 1.33 | 1.31 | 0.89
|  |  | Health | Comm/Ind Work (Precision) | HealthComm/Ind Work (Precision) | 3438 | 0.65 | 0.64 | 0.4 | Other | Heat Pump | OtherHeat Pump | 0.93 | 1.33 | 1.31 | 0.61
Exterior Space Type Dropdown |  |  | Health | Conference Room | HealthConference Room | 1201 | 0.28 | 0.3 | 0.16 | Other | Heat Pump/ Unconditioned | OtherHeat Pump/ Unconditioned | 1 | 1.33 | 1.31 | 1
Parking Garage |  |  | Health | Convention and Meeting Center | HealthConvention and Meeting Center | 3438 | 0.65 | 0.64 | 0.4 | Other | Heat Pump/ Unknown | OtherHeat Pump/ Unknown | 1 | 1.33 | 1.31 | 0.89
Non Rebated Area |  |  | Health | Copy Room | HealthCopy Room | 2964 | 0.59 | 0.61 | 0.41 | Other | NoAC/ ElecRes | OtherNoAC/ ElecRes | 0.74 | 1 | 1 | 0.2
Other Unlisted Activity Types |  |  | Health | Corridor/Hallways | HealthCorridor/Hallways | 6191 | 0.9 | 0.9 | 0.77 | Other | NoAC/ NonElec | OtherNoAC/ NonElec | 1 | 1 | 1 | 1
Outside/Outdoor Area |  |  | Health | Courtrooms | HealthCourtrooms | 3438 | 0.65 | 0.64 | 0.4 | Other | NoAC/ Unconditioned | OtherNoAC/ Unconditioned | 1 | 1 | 1 | 1
|  |  | Health | Dining Area | HealthDining Area | 2962 | 0.48 | 0.53 | 0.51 | Other | NoAC/ Unknown | OtherNoAC/ Unknown | 1 | 1 | 1 | 0.89
Exterior Cooling Type |  |  | Health | Dry Cleaning | HealthDry Cleaning | 3438 | 0.65 | 0.64 | 0.4 | Other | Unknown/ ElecRes | OtherUnknown/ ElecRes | 1 | 1 | 1 | 0.2
Not Air Conditioned |  |  | Health | Exercise Centers/Gymnasium | HealthExercise Centers/Gymnasium | 4833 | 0.81 | 0.82 | 0.6 | Other | Unknown/ NonElec | OtherUnknown/ NonElec | 1 | 1 | 1 | 1
|  |  | Health | Exhibit Display Area/Museum | HealthExhibit Display Area/Museum | 2964 | 0.59 | 0.61 | 0.41 | Other | Unknown/ Unconditioned | OtherUnknown/ Unconditioned | 1 | 1 | 1 | 1
Exterior Heating Type |  |  | Health | Guest Room (Hotel/Motel) | HealthGuest Room (Hotel/Motel) | 3438 | 0.65 | 0.64 | 0.4 | Other | Unknown/ Unknown | OtherUnknown/ Unknown | 1 | 1 | 1 | 0.89
Unconditioned |  |  | Health | Kitchen/Break room & Food Prep | HealthKitchen/Break room & Food Prep | 3522 | 0.79 | 0.74 | 0.42 | Other | Refrigerated/ Unconditioned | OtherRefrigerated/ Unconditioned | 1.41 | 1.4 | 1.4 | 1.4
|  |  | Health | Laboratory | HealthLaboratory | 3438 | 0.65 | 0.64 | 0.4 | Other | Freezer/ Unconditioned | OtherFreezer/ Unconditioned | 1.52 | 1.51 | 1.51 | 1.51
|  |  | Health | Laundry | HealthLaundry | 2964 | 0.59 | 0.61 | 0.41
|  |  | Health | Library | HealthLibrary | 1957 | 0.44 | 0.46 | 0.31
|  |  | Health | Loading Dock | HealthLoading Dock | 7358 | 0.97 | 0.97 | 0.62
|  |  | Health | Lobby (Hotel) | HealthLobby (Hotel) | 3438 | 0.65 | 0.64 | 0.4
|  |  | Health | Lobby (Main Entry and Assembly) | HealthLobby (Main Entry and Assembly) | 5947 | 0.83 | 0.82 | 0.71
|  |  | Health | Lobby (Office Reception/Waiting) | HealthLobby (Office Reception/Waiting) | 3425 | 0.84 | 0.87 | 0.49
|  |  | Health | Locker and Dressing Room | HealthLocker and Dressing Room | 2964 | 0.59 | 0.61 | 0.41
|  |  | Health | Mall Arcade and Atrium | HealthMall Arcade and Atrium | 3438 | 0.65 | 0.64 | 0.4
|  |  | Health | Mechanical/Electrical Room | HealthMechanical/Electrical Room | 5026 | 0.73 | 0.74 | 0.46
|  |  | Health | Medical Offices and Exam rooms | HealthMedical Offices and Exam rooms | 2964 | 0.59 | 0.61 | 0.41
|  |  | Health | Office (Executive/Private) | HealthOffice (Executive/Private) | 1753 | 0.42 | 0.44 | 0.2
|  |  | Health | Office (General) | HealthOffice (General) | 3001 | 0.67 | 0.67 | 0.43
|  |  | Health | Office(Open Plan) | HealthOffice(Open Plan) | 3159 | 0.81 | 0.82 | 0.49
|  |  | Health | Patient Rooms | HealthPatient Rooms | 2964 | 0.59 | 0.61 | 0.41
|  |  | Health | Patio Area | HealthPatio Area | 3438 | 0.65 | 0.64 | 0.4
|  |  | Health | Pool/Spa Area | HealthPool/Spa Area | 3438 | 0.65 | 0.64 | 0.4
|  |  | Health | Police/Fire Station | HealthPolice/Fire Station | 3438 | 0.65 | 0.64 | 0.4
|  |  | Health | Religious Worship | HealthReligious Worship | 3438 | 0.65 | 0.64 | 0.4
|  |  | Health | Residential | HealthResidential | 3438 | 0.65 | 0.64 | 0.4
|  |  | Health | Restrooms | HealthRestrooms | 2521 | 0.48 | 0.42 | 0.3
|  |  | Health | Retail Sales/Showroom | HealthRetail Sales/Showroom | 6152 | 0.97 | 0.97 | 0.78
|  |  | Health | Smoking Lounge | HealthSmoking Lounge | 3438 | 0.65 | 0.64 | 0.4
|  |  | Health | Storage (Conditioned) | HealthStorage (Conditioned) | 2964 | 0.59 | 0.61 | 0.41
|  |  | Health | Storage (Unconditioned) | HealthStorage (Unconditioned) | 2930 | 0.66 | 0.64 | 0.4
|  |  | Health | Storage (Refrigerated/Freezer),Walk-in | HealthStorage (Refrigerated/Freezer),Walk-in | 4672 | 0.81 | 0.81 | 0.44
|  |  | Health | Storage (Refrigerated/Freezer),Building | HealthStorage (Refrigerated/Freezer),Building | 3438 | 0.65 | 0.64 | 0.4
|  |  | Health | Surgery Rooms | HealthSurgery Rooms | 3438 | 0.65 | 0.64 | 0.4
|  |  | Health | Theater (Motion Picture) | HealthTheater (Motion Picture) | 3438 | 0.65 | 0.64 | 0.4
|  |  | Health | Theater (Performance) | HealthTheater (Performance) | 3438 | 0.65 | 0.64 | 0.4
|  |  | Health | Unknown | HealthUnknown | 3438 | 0.65 | 0.64 | 0.4
|  |  | Health | Vacant (Condtioned) | HealthVacant (Condtioned) | 3438 | 0.65 | 0.64 | 0.4
|  |  | Health | Vacant (Unconditioned) | HealthVacant (Unconditioned) | 3438 | 0.65 | 0.64 | 0.4
|  |  | Health | Vocational Areas | HealthVocational Areas | 3438 | 0.65 | 0.64 | 0.4
|  |  | Health | Parking Garage | HealthParking Garage | 8678 | 0.98 | 0.98 | 0.99
|  |  | Health | Non Rebated Area | HealthNon Rebated Area | 3438 | 0.65 | 0.64 | 0.4
|  |  | Health | Other Unlisted Activity Types | HealthOther Unlisted Activity Types | 2964 | 0.59 | 0.61 | 0.41
|  |  | Health | Outside/Outdoor Area | HealthOutside/Outdoor Area | 3604 | 0.11 | 0.11 | 0.58
|  |  | Office | Auditorium/Gym | OfficeAuditorium/Gym | 3438 | 0.65 | 0.64 | 0.4
|  |  | Office | Auto Repair Workshop | OfficeAuto Repair Workshop | 6189 | 0.88 | 0.89 | 0.61
|  |  | Office | Bank/Financial | OfficeBank/Financial | 3438 | 0.65 | 0.64 | 0.4
|  |  | Office | Bar Cocktail Lounge | OfficeBar Cocktail Lounge | 3438 | 0.65 | 0.64 | 0.4
|  |  | Office | Barber/Beauty Shop | OfficeBarber/Beauty Shop | 3438 | 0.65 | 0.64 | 0.4
|  |  | Office | Casino/Gaming | OfficeCasino/Gaming | 3438 | 0.65 | 0.64 | 0.4
|  |  | Office | Classroom/Lecture | OfficeClassroom/Lecture | 1584 | 0.24 | 0.24 | 0.2
|  |  | Office | Clean Room | OfficeClean Room | 3438 | 0.65 | 0.64 | 0.4
|  |  | Office | Computer Room/Data Processing | OfficeComputer Room/Data Processing | 2897 | 0.7 | 0.69 | 0.48
|  |  | Office | Comm/Ind Work(General High Bay flr-to-clng ht >= 25ft) | OfficeComm/Ind Work(General High Bay flr-to-clng ht >= 25ft) | 4790 | 0.9 | 0.91 | 0.82
|  |  | Office | Comm/Ind Work(General Low Bay flr-to-clng ht < 25ft) | OfficeComm/Ind Work(General Low Bay flr-to-clng ht < 25ft) | 6775 | 0.95 | 0.95 | 0.77
|  |  | Office | Comm/Ind Work (Precision) | OfficeComm/Ind Work (Precision) | 3438 | 0.65 | 0.64 | 0.4
|  |  | Office | Conference Room | OfficeConference Room | 1201 | 0.28 | 0.3 | 0.16
|  |  | Office | Convention and Meeting Center | OfficeConvention and Meeting Center | 3438 | 0.65 | 0.64 | 0.4
|  |  | Office | Copy Room | OfficeCopy Room | 2897 | 0.7 | 0.69 | 0.48
|  |  | Office | Corridor/Hallways | OfficeCorridor/Hallways | 4092 | 0.65 | 0.64 | 0.71
|  |  | Office | Courtrooms | OfficeCourtrooms | 3438 | 0.65 | 0.64 | 0.4
|  |  | Office | Dining Area | OfficeDining Area | 2962 | 0.48 | 0.53 | 0.51
|  |  | Office | Dry Cleaning | OfficeDry Cleaning | 3438 | 0.65 | 0.64 | 0.4
|  |  | Office | Exercise Centers/Gymnasium | OfficeExercise Centers/Gymnasium | 4833 | 0.81 | 0.82 | 0.6
|  |  | Office | Exhibit Display Area/Museum | OfficeExhibit Display Area/Museum | 3438 | 0.65 | 0.64 | 0.4
|  |  | Office | Guest Room (Hotel/Motel) | OfficeGuest Room (Hotel/Motel) | 3438 | 0.65 | 0.64 | 0.4
|  |  | Office | Kitchen/Break room & Food Prep | OfficeKitchen/Break room & Food Prep | 3522 | 0.79 | 0.74 | 0.42
|  |  | Office | Laboratory | OfficeLaboratory | 3438 | 0.65 | 0.64 | 0.4
|  |  | Office | Laundry | OfficeLaundry | 3438 | 0.65 | 0.64 | 0.4
|  |  | Office | Library | OfficeLibrary | 1957 | 0.44 | 0.46 | 0.31
|  |  | Office | Loading Dock | OfficeLoading Dock | 7358 | 0.97 | 0.97 | 0.62
|  |  | Office | Lobby (Hotel) | OfficeLobby (Hotel) | 3438 | 0.65 | 0.64 | 0.4
|  |  | Office | Lobby (Main Entry and Assembly) | OfficeLobby (Main Entry and Assembly) | 6569 | 0.93 | 0.91 | 0.8
|  |  | Office | Lobby (Office Reception/Waiting) | OfficeLobby (Office Reception/Waiting) | 3425 | 0.84 | 0.87 | 0.49
|  |  | Office | Locker and Dressing Room | OfficeLocker and Dressing Room | 3438 | 0.65 | 0.64 | 0.4
|  |  | Office | Mall Arcade and Atrium | OfficeMall Arcade and Atrium | 3438 | 0.65 | 0.64 | 0.4
|  |  | Office | Mechanical/Electrical Room | OfficeMechanical/Electrical Room | 5026 | 0.73 | 0.74 | 0.46
|  |  | Office | Medical Offices and Exam rooms | OfficeMedical Offices and Exam rooms | 3438 | 0.65 | 0.64 | 0.4
|  |  | Office | Office (Executive/Private) | OfficeOffice (Executive/Private) | 1753 | 0.42 | 0.44 | 0.2
|  |  | Office | Office (General) | OfficeOffice (General) | 3009 | 0.7 | 0.7 | 0.48
|  |  | Office | Office(Open Plan) | OfficeOffice(Open Plan) | 3159 | 0.81 | 0.82 | 0.49
|  |  | Office | Patient Rooms | OfficePatient Rooms | 3438 | 0.65 | 0.64 | 0.4
|  |  | Office | Patio Area | OfficePatio Area | 3438 | 0.65 | 0.64 | 0.4
|  |  | Office | Pool/Spa Area | OfficePool/Spa Area | 3438 | 0.65 | 0.64 | 0.4
|  |  | Office | Police/Fire Station | OfficePolice/Fire Station | 3438 | 0.65 | 0.64 | 0.4
|  |  | Office | Religious Worship | OfficeReligious Worship | 3438 | 0.65 | 0.64 | 0.4
|  |  | Office | Residential | OfficeResidential | 3438 | 0.65 | 0.64 | 0.4
|  |  | Office | Restrooms | OfficeRestrooms | 2521 | 0.48 | 0.42 | 0.3
|  |  | Office | Retail Sales/Showroom | OfficeRetail Sales/Showroom | 6152 | 0.97 | 0.97 | 0.78
|  |  | Office | Smoking Lounge | OfficeSmoking Lounge | 2897 | 0.7 | 0.69 | 0.48
|  |  | Office | Storage (Conditioned) | OfficeStorage (Conditioned) | 2897 | 0.7 | 0.69 | 0.48
|  |  | Office | Storage (Unconditioned) | OfficeStorage (Unconditioned) | 2930 | 0.66 | 0.64 | 0.4
|  |  | Office | Storage (Refrigerated/Freezer),Walk-in | OfficeStorage (Refrigerated/Freezer),Walk-in | 4672 | 0.81 | 0.81 | 0.44
|  |  | Office | Storage (Refrigerated/Freezer),Building | OfficeStorage (Refrigerated/Freezer),Building | 3438 | 0.65 | 0.64 | 0.4
|  |  | Office | Surgery Rooms | OfficeSurgery Rooms | 3438 | 0.65 | 0.64 | 0.4
|  |  | Office | Theater (Motion Picture) | OfficeTheater (Motion Picture) | 3438 | 0.65 | 0.64 | 0.4
|  |  | Office | Theater (Performance) | OfficeTheater (Performance) | 3438 | 0.65 | 0.64 | 0.4
|  |  | Office | Unknown | OfficeUnknown | 3438 | 0.65 | 0.64 | 0.4
|  |  | Office | Vacant (Condtioned) | OfficeVacant (Condtioned) | 3438 | 0.65 | 0.64 | 0.4
|  |  | Office | Vacant (Unconditioned) | OfficeVacant (Unconditioned) | 3438 | 0.65 | 0.64 | 0.4
|  |  | Office | Vocational Areas | OfficeVocational Areas | 3438 | 0.65 | 0.64 | 0.4
|  |  | Office | Parking Garage | OfficeParking Garage | 8678 | 0.98 | 0.98 | 0.99
|  |  | Office | Non Rebated Area | OfficeNon Rebated Area | 3438 | 0.65 | 0.64 | 0.4
|  |  | Office | Other Unlisted Activity Types | OfficeOther Unlisted Activity Types | 2897 | 0.7 | 0.69 | 0.48
|  |  | Office | Outside/Outdoor Area | OfficeOutside/Outdoor Area | 3604 | 0.11 | 0.11 | 0.58
|  |  | Retail | Auditorium/Gym | RetailAuditorium/Gym | 3438 | 0.65 | 0.64 | 0.4
|  |  | Retail | Auto Repair Workshop | RetailAuto Repair Workshop | 6189 | 0.88 | 0.89 | 0.61
|  |  | Retail | Bank/Financial | RetailBank/Financial | 3438 | 0.65 | 0.64 | 0.4
|  |  | Retail | Bar Cocktail Lounge | RetailBar Cocktail Lounge | 3438 | 0.65 | 0.64 | 0.4
|  |  | Retail | Barber/Beauty Shop | RetailBarber/Beauty Shop | 3438 | 0.65 | 0.64 | 0.4
|  |  | Retail | Casino/Gaming | RetailCasino/Gaming | 3438 | 0.65 | 0.64 | 0.4
|  |  | Retail | Classroom/Lecture | RetailClassroom/Lecture | 1584 | 0.24 | 0.24 | 0.2
|  |  | Retail | Clean Room | RetailClean Room | 3438 | 0.65 | 0.64 | 0.4
|  |  | Retail | Computer Room/Data Processing | RetailComputer Room/Data Processing | 3438 | 0.65 | 0.64 | 0.4
|  |  | Retail | Comm/Ind Work(General High Bay flr-to-clng ht >= 25ft) | RetailComm/Ind Work(General High Bay flr-to-clng ht >= 25ft) | 4790 | 0.9 | 0.91 | 0.82
|  |  | Retail | Comm/Ind Work(General Low Bay flr-to-clng ht < 25ft) | RetailComm/Ind Work(General Low Bay flr-to-clng ht < 25ft) | 6775 | 0.95 | 0.95 | 0.77
|  |  | Retail | Comm/Ind Work (Precision) | RetailComm/Ind Work (Precision) | 3438 | 0.65 | 0.64 | 0.4
|  |  | Retail | Conference Room | RetailConference Room | 1201 | 0.28 | 0.3 | 0.16
|  |  | Retail | Convention and Meeting Center | RetailConvention and Meeting Center | 3438 | 0.65 | 0.64 | 0.4
|  |  | Retail | Copy Room | RetailCopy Room | 3438 | 0.65 | 0.64 | 0.4
|  |  | Retail | Corridor/Hallways | RetailCorridor/Hallways | 5670 | 0.86 | 0.86 | 0.73
|  |  | Retail | Courtrooms | RetailCourtrooms | 3438 | 0.65 | 0.64 | 0.4
|  |  | Retail | Dining Area | RetailDining Area | 2962 | 0.48 | 0.53 | 0.51
|  |  | Retail | Dry Cleaning | RetailDry Cleaning | 4393 | 0.74 | 0.74 | 0.51
|  |  | Retail | Exercise Centers/Gymnasium | RetailExercise Centers/Gymnasium | 4833 | 0.81 | 0.82 | 0.6
|  |  | Retail | Exhibit Display Area/Museum | RetailExhibit Display Area/Museum | 3438 | 0.65 | 0.64 | 0.4
|  |  | Retail | Guest Room (Hotel/Motel) | RetailGuest Room (Hotel/Motel) | 3438 | 0.65 | 0.64 | 0.4
|  |  | Retail | Kitchen/Break room & Food Prep | RetailKitchen/Break room & Food Prep | 3522 | 0.79 | 0.74 | 0.42
|  |  | Retail | Laboratory | RetailLaboratory | 3438 | 0.65 | 0.64 | 0.4
|  |  | Retail | Laundry | RetailLaundry | 3438 | 0.65 | 0.64 | 0.4
|  |  | Retail | Library | RetailLibrary | 1957 | 0.44 | 0.46 | 0.31
|  |  | Retail | Loading Dock | RetailLoading Dock | 7358 | 0.97 | 0.97 | 0.62
|  |  | Retail | Lobby (Hotel) | RetailLobby (Hotel) | 3438 | 0.65 | 0.64 | 0.4
|  |  | Retail | Lobby (Main Entry and Assembly) | RetailLobby (Main Entry and Assembly) | 6417 | 0.99 | 0.99 | 0.63
|  |  | Retail | Lobby (Office Reception/Waiting) | RetailLobby (Office Reception/Waiting) | 3425 | 0.84 | 0.87 | 0.49
|  |  | Retail | Locker and Dressing Room | RetailLocker and Dressing Room | 3438 | 0.65 | 0.64 | 0.4
|  |  | Retail | Mall Arcade and Atrium | RetailMall Arcade and Atrium | 3438 | 0.65 | 0.64 | 0.4
|  |  | Retail | Mechanical/Electrical Room | RetailMechanical/Electrical Room | 5026 | 0.73 | 0.74 | 0.46
|  |  | Retail | Medical Offices and Exam rooms | RetailMedical Offices and Exam rooms | 3438 | 0.65 | 0.64 | 0.4
|  |  | Retail | Office (Executive/Private) | RetailOffice (Executive/Private) | 1753 | 0.42 | 0.44 | 0.2
|  |  | Retail | Office (General) | RetailOffice (General) | 3175 | 0.72 | 0.73 | 0.4
|  |  | Retail | Office(Open Plan) | RetailOffice(Open Plan) | 3159 | 0.81 | 0.82 | 0.49
|  |  | Retail | Patient Rooms | RetailPatient Rooms | 3438 | 0.65 | 0.64 | 0.4
|  |  | Retail | Patio Area | RetailPatio Area | 3438 | 0.65 | 0.64 | 0.4
|  |  | Retail | Pool/Spa Area | RetailPool/Spa Area | 3438 | 0.65 | 0.64 | 0.4
|  |  | Retail | Police/Fire Station | RetailPolice/Fire Station | 3438 | 0.65 | 0.64 | 0.4
|  |  | Retail | Religious Worship | RetailReligious Worship | 3438 | 0.65 | 0.64 | 0.4
|  |  | Retail | Residential | RetailResidential | 3438 | 0.65 | 0.64 | 0.4
|  |  | Retail | Restrooms | RetailRestrooms | 5816 | 0.94 | 0.94 | 0.7
|  |  | Retail | Retail Sales/Showroom | RetailRetail Sales/Showroom | 5192 | 0.98 | 0.98 | 0.64
|  |  | Retail | Smoking Lounge | RetailSmoking Lounge | 3438 | 0.65 | 0.64 | 0.4
|  |  | Retail | Storage (Conditioned) | RetailStorage (Conditioned) | 4393 | 0.74 | 0.74 | 0.51
|  |  | Retail | Storage (Unconditioned) | RetailStorage (Unconditioned) | 2930 | 0.66 | 0.64 | 0.4
|  |  | Retail | Storage (Refrigerated/Freezer),Walk-in | RetailStorage (Refrigerated/Freezer),Walk-in | 4672 | 0.81 | 0.81 | 0.44
|  |  | Retail | Storage (Refrigerated/Freezer),Building | RetailStorage (Refrigerated/Freezer),Building | 3438 | 0.65 | 0.64 | 0.4
|  |  | Retail | Surgery Rooms | RetailSurgery Rooms | 3438 | 0.65 | 0.64 | 0.4
|  |  | Retail | Theater (Motion Picture) | RetailTheater (Motion Picture) | 3438 | 0.65 | 0.64 | 0.4
|  |  | Retail | Theater (Performance) | RetailTheater (Performance) | 3438 | 0.65 | 0.64 | 0.4
|  |  | Retail | Unknown | RetailUnknown | 3438 | 0.65 | 0.64 | 0.4
|  |  | Retail | Vacant (Condtioned) | RetailVacant (Condtioned) | 3438 | 0.65 | 0.64 | 0.4
|  |  | Retail | Vacant (Unconditioned) | RetailVacant (Unconditioned) | 3438 | 0.65 | 0.64 | 0.4
|  |  | Retail | Vocational Areas | RetailVocational Areas | 3438 | 0.65 | 0.64 | 0.4
|  |  | Retail | Parking Garage | RetailParking Garage | 8678 | 0.98 | 0.98 | 0.99
|  |  | Retail | Non Rebated Area | RetailNon Rebated Area | 3438 | 0.65 | 0.64 | 0.4
|  |  | Retail | Other Unlisted Activity Types | RetailOther Unlisted Activity Types | 4393 | 0.74 | 0.74 | 0.51
|  |  | Retail | Outside/Outdoor Area | RetailOutside/Outdoor Area | 3604 | 0.11 | 0.11 | 0.58
|  |  | School | Auditorium/Gym | SchoolAuditorium/Gym | 2032 | 0.33 | 0.34 | 0.35
|  |  | School | Auto Repair Workshop | SchoolAuto Repair Workshop | 6189 | 0.88 | 0.89 | 0.61
|  |  | School | Bank/Financial | SchoolBank/Financial | 3438 | 0.65 | 0.64 | 0.4
|  |  | School | Bar Cocktail Lounge | SchoolBar Cocktail Lounge | 3438 | 0.65 | 0.64 | 0.4
|  |  | School | Barber/Beauty Shop | SchoolBarber/Beauty Shop | 3438 | 0.65 | 0.64 | 0.4
|  |  | School | Casino/Gaming | SchoolCasino/Gaming | 3438 | 0.65 | 0.64 | 0.4
|  |  | School | Classroom/Lecture | SchoolClassroom/Lecture | 1505 | 0.21 | 0.22 | 0.2
|  |  | School | Clean Room | SchoolClean Room | 3438 | 0.65 | 0.64 | 0.4
|  |  | School | Computer Room/Data Processing | SchoolComputer Room/Data Processing | 2032 | 0.33 | 0.34 | 0.35
|  |  | School | Comm/Ind Work(General High Bay flr-to-clng ht >= 25ft) | SchoolComm/Ind Work(General High Bay flr-to-clng ht >= 25ft) | 4790 | 0.9 | 0.91 | 0.82
|  |  | School | Comm/Ind Work(General Low Bay flr-to-clng ht < 25ft) | SchoolComm/Ind Work(General Low Bay flr-to-clng ht < 25ft) | 6775 | 0.95 | 0.95 | 0.77
|  |  | School | Comm/Ind Work (Precision) | SchoolComm/Ind Work (Precision) | 3438 | 0.65 | 0.64 | 0.4
|  |  | School | Conference Room | SchoolConference Room | 1201 | 0.28 | 0.3 | 0.16
|  |  | School | Convention and Meeting Center | SchoolConvention and Meeting Center | 3438 | 0.65 | 0.64 | 0.4
|  |  | School | Copy Room | SchoolCopy Room | 3438 | 0.65 | 0.64 | 0.4
|  |  | School | Corridor/Hallways | SchoolCorridor/Hallways | 5052 | 0.77 | 0.78 | 0.75
|  |  | School | Courtrooms | SchoolCourtrooms | 3438 | 0.65 | 0.64 | 0.4
|  |  | School | Dining Area | SchoolDining Area | 2962 | 0.48 | 0.53 | 0.51
|  |  | School | Dry Cleaning | SchoolDry Cleaning | 3438 | 0.65 | 0.64 | 0.4
|  |  | School | Exercise Centers/Gymnasium | SchoolExercise Centers/Gymnasium | 4833 | 0.81 | 0.82 | 0.6
|  |  | School | Exhibit Display Area/Museum | SchoolExhibit Display Area/Museum | 3438 | 0.65 | 0.64 | 0.4
|  |  | School | Guest Room (Hotel/Motel) | SchoolGuest Room (Hotel/Motel) | 3438 | 0.65 | 0.64 | 0.4
|  |  | School | Kitchen/Break room & Food Prep | SchoolKitchen/Break room & Food Prep | 3522 | 0.79 | 0.74 | 0.42
|  |  | School | Laboratory | SchoolLaboratory | 3438 | 0.65 | 0.64 | 0.4
|  |  | School | Laundry | SchoolLaundry | 3438 | 0.65 | 0.64 | 0.4
|  |  | School | Library | SchoolLibrary | 1957 | 0.44 | 0.46 | 0.31
|  |  | School | Loading Dock | SchoolLoading Dock | 7358 | 0.97 | 0.97 | 0.62
|  |  | School | Lobby (Hotel) | SchoolLobby (Hotel) | 3438 | 0.65 | 0.64 | 0.4
|  |  | School | Lobby (Main Entry and Assembly) | SchoolLobby (Main Entry and Assembly) | 5947 | 0.83 | 0.82 | 0.71
|  |  | School | Lobby (Office Reception/Waiting) | SchoolLobby (Office Reception/Waiting) | 3425 | 0.84 | 0.87 | 0.49
|  |  | School | Locker and Dressing Room | SchoolLocker and Dressing Room | 2032 | 0.33 | 0.34 | 0.35
|  |  | School | Mall Arcade and Atrium | SchoolMall Arcade and Atrium | 3438 | 0.65 | 0.64 | 0.4
|  |  | School | Mechanical/Electrical Room | SchoolMechanical/Electrical Room | 5026 | 0.73 | 0.74 | 0.46
|  |  | School | Medical Offices and Exam rooms | SchoolMedical Offices and Exam rooms | 3438 | 0.65 | 0.64 | 0.4
|  |  | School | Office (Executive/Private) | SchoolOffice (Executive/Private) | 2084 | 0.42 | 0.57 | 0.26
|  |  | School | Office (General) | SchoolOffice (General) | 4252 | 0.66 | 0.67 | 0.46
|  |  | School | Office(Open Plan) | SchoolOffice(Open Plan) | 2888 | 0.62 | 0.7 | 0.54
|  |  | School | Patient Rooms | SchoolPatient Rooms | 3438 | 0.65 | 0.64 | 0.4
|  |  | School | Patio Area | SchoolPatio Area | 3438 | 0.65 | 0.64 | 0.4
|  |  | School | Pool/Spa Area | SchoolPool/Spa Area | 3438 | 0.65 | 0.64 | 0.4
|  |  | School | Police/Fire Station | SchoolPolice/Fire Station | 3438 | 0.65 | 0.64 | 0.4
|  |  | School | Religious Worship | SchoolReligious Worship | 3438 | 0.65 | 0.64 | 0.4
|  |  | School | Residential | SchoolResidential | 2032 | 0.33 | 0.34 | 0.35
|  |  | School | Restrooms | SchoolRestrooms | 2521 | 0.48 | 0.42 | 0.3
|  |  | School | Retail Sales/Showroom | SchoolRetail Sales/Showroom | 6152 | 0.97 | 0.97 | 0.78
|  |  | School | Smoking Lounge | SchoolSmoking Lounge | 3438 | 0.65 | 0.64 | 0.4
|  |  | School | Storage (Conditioned) | SchoolStorage (Conditioned) | 2032 | 0.33 | 0.34 | 0.35
|  |  | School | Storage (Unconditioned) | SchoolStorage (Unconditioned) | 2930 | 0.66 | 0.64 | 0.4
|  |  | School | Storage (Refrigerated/Freezer),Walk-in | SchoolStorage (Refrigerated/Freezer),Walk-in | 4672 | 0.81 | 0.81 | 0.44
|  |  | School | Storage (Refrigerated/Freezer),Building | SchoolStorage (Refrigerated/Freezer),Building | 3438 | 0.65 | 0.64 | 0.4
|  |  | School | Surgery Rooms | SchoolSurgery Rooms | 3438 | 0.65 | 0.64 | 0.4
|  |  | School | Theater (Motion Picture) | SchoolTheater (Motion Picture) | 3438 | 0.65 | 0.64 | 0.4
|  |  | School | Theater (Performance) | SchoolTheater (Performance) | 3438 | 0.65 | 0.64 | 0.4
|  |  | School | Unknown | SchoolUnknown | 3438 | 0.65 | 0.64 | 0.4
|  |  | School | Vacant (Condtioned) | SchoolVacant (Condtioned) | 2032 | 0.33 | 0.34 | 0.35
|  |  | School | Vacant (Unconditioned) | SchoolVacant (Unconditioned) | 3438 | 0.65 | 0.64 | 0.4
|  |  | School | Vocational Areas | SchoolVocational Areas | 3438 | 0.65 | 0.64 | 0.4
|  |  | School | Parking Garage | SchoolParking Garage | 8678 | 0.98 | 0.98 | 0.99
|  |  | School | Non Rebated Area | SchoolNon Rebated Area | 3438 | 0.65 | 0.64 | 0.4
|  |  | School | Other Unlisted Activity Types | SchoolOther Unlisted Activity Types | 2032 | 0.33 | 0.34 | 0.35
|  |  | School | Outside/Outdoor Area | SchoolOutside/Outdoor Area | 3604 | 0.11 | 0.11 | 0.58
|  |  | Warehouse_Industrial | Auditorium/Gym | Warehouse_IndustrialAuditorium/Gym | 3438 | 0.65 | 0.64 | 0.4
|  |  | Warehouse_Industrial | Auto Repair Workshop | Warehouse_IndustrialAuto Repair Workshop | 5482 | 0.94 | 0.93 | 0.49
|  |  | Warehouse_Industrial | Bank/Financial | Warehouse_IndustrialBank/Financial | 3438 | 0.65 | 0.64 | 0.4
|  |  | Warehouse_Industrial | Bar Cocktail Lounge | Warehouse_IndustrialBar Cocktail Lounge | 3438 | 0.65 | 0.64 | 0.4
|  |  | Warehouse_Industrial | Barber/Beauty Shop | Warehouse_IndustrialBarber/Beauty Shop | 3438 | 0.65 | 0.64 | 0.4
|  |  | Warehouse_Industrial | Casino/Gaming | Warehouse_IndustrialCasino/Gaming | 3438 | 0.65 | 0.64 | 0.4
|  |  | Warehouse_Industrial | Classroom/Lecture | Warehouse_IndustrialClassroom/Lecture | 1584 | 0.24 | 0.24 | 0.2
|  |  | Warehouse_Industrial | Clean Room | Warehouse_IndustrialClean Room | 3438 | 0.65 | 0.64 | 0.4
|  |  | Warehouse_Industrial | Computer Room/Data Processing | Warehouse_IndustrialComputer Room/Data Processing | 3438 | 0.65 | 0.64 | 0.4
|  |  | Warehouse_Industrial | Comm/Ind Work(General High Bay flr-to-clng ht >= 25ft) | Warehouse_IndustrialComm/Ind Work(General High Bay flr-to-clng ht >= 25ft) | 5103 | 0.92 | 0.94 | 0.86
|  |  | Warehouse_Industrial | Comm/Ind Work(General Low Bay flr-to-clng ht < 25ft) | Warehouse_IndustrialComm/Ind Work(General Low Bay flr-to-clng ht < 25ft) | 7110 | 0.98 | 0.98 | 0.78
|  |  | Warehouse_Industrial | Comm/Ind Work (Precision) | Warehouse_IndustrialComm/Ind Work (Precision) | 3338 | 0.71 | 0.69 | 0.44
|  |  | Warehouse_Industrial | Conference Room | Warehouse_IndustrialConference Room | 1201 | 0.28 | 0.3 | 0.16
|  |  | Warehouse_Industrial | Convention and Meeting Center | Warehouse_IndustrialConvention and Meeting Center | 3438 | 0.65 | 0.64 | 0.4
|  |  | Warehouse_Industrial | Copy Room | Warehouse_IndustrialCopy Room | 3438 | 0.65 | 0.64 | 0.4
|  |  | Warehouse_Industrial | Corridor/Hallways | Warehouse_IndustrialCorridor/Hallways | 5670 | 0.86 | 0.86 | 0.73
|  |  | Warehouse_Industrial | Courtrooms | Warehouse_IndustrialCourtrooms | 3438 | 0.65 | 0.64 | 0.4
|  |  | Warehouse_Industrial | Dining Area | Warehouse_IndustrialDining Area | 2962 | 0.48 | 0.53 | 0.51
|  |  | Warehouse_Industrial | Dry Cleaning | Warehouse_IndustrialDry Cleaning | 3438 | 0.65 | 0.64 | 0.4
|  |  | Warehouse_Industrial | Exercise Centers/Gymnasium | Warehouse_IndustrialExercise Centers/Gymnasium | 4833 | 0.81 | 0.82 | 0.6
|  |  | Warehouse_Industrial | Exhibit Display Area/Museum | Warehouse_IndustrialExhibit Display Area/Museum | 3438 | 0.65 | 0.64 | 0.4
|  |  | Warehouse_Industrial | Guest Room (Hotel/Motel) | Warehouse_IndustrialGuest Room (Hotel/Motel) | 3438 | 0.65 | 0.64 | 0.4
|  |  | Warehouse_Industrial | Kitchen/Break room & Food Prep | Warehouse_IndustrialKitchen/Break room & Food Prep | 3522 | 0.79 | 0.74 | 0.42
|  |  | Warehouse_Industrial | Laboratory | Warehouse_IndustrialLaboratory | 3438 | 0.65 | 0.64 | 0.4
|  |  | Warehouse_Industrial | Laundry | Warehouse_IndustrialLaundry | 3438 | 0.65 | 0.64 | 0.4
|  |  | Warehouse_Industrial | Library | Warehouse_IndustrialLibrary | 1957 | 0.44 | 0.46 | 0.31
|  |  | Warehouse_Industrial | Loading Dock | Warehouse_IndustrialLoading Dock | 7358 | 0.97 | 0.97 | 0.62
|  |  | Warehouse_Industrial | Lobby (Hotel) | Warehouse_IndustrialLobby (Hotel) | 3438 | 0.65 | 0.64 | 0.4
|  |  | Warehouse_Industrial | Lobby (Main Entry and Assembly) | Warehouse_IndustrialLobby (Main Entry and Assembly) | 5947 | 0.83 | 0.82 | 0.71
|  |  | Warehouse_Industrial | Lobby (Office Reception/Waiting) | Warehouse_IndustrialLobby (Office Reception/Waiting) | 3425 | 0.84 | 0.87 | 0.49
|  |  | Warehouse_Industrial | Locker and Dressing Room | Warehouse_IndustrialLocker and Dressing Room | 3438 | 0.65 | 0.64 | 0.4
|  |  | Warehouse_Industrial | Mall Arcade and Atrium | Warehouse_IndustrialMall Arcade and Atrium | 3438 | 0.65 | 0.64 | 0.4
|  |  | Warehouse_Industrial | Mechanical/Electrical Room | Warehouse_IndustrialMechanical/Electrical Room | 5026 | 0.73 | 0.74 | 0.46
|  |  | Warehouse_Industrial | Medical Offices and Exam rooms | Warehouse_IndustrialMedical Offices and Exam rooms | 3438 | 0.65 | 0.64 | 0.4
|  |  | Warehouse_Industrial | Office (Executive/Private) | Warehouse_IndustrialOffice (Executive/Private) | 1753 | 0.42 | 0.44 | 0.2
|  |  | Warehouse_Industrial | Office (General) | Warehouse_IndustrialOffice (General) | 2868 | 0.74 | 0.74 | 0.36
|  |  | Warehouse_Industrial | Office(Open Plan) | Warehouse_IndustrialOffice(Open Plan) | 3159 | 0.81 | 0.82 | 0.49
|  |  | Warehouse_Industrial | Patient Rooms | Warehouse_IndustrialPatient Rooms | 3438 | 0.65 | 0.64 | 0.4
|  |  | Warehouse_Industrial | Patio Area | Warehouse_IndustrialPatio Area | 3438 | 0.65 | 0.64 | 0.4
|  |  | Warehouse_Industrial | Pool/Spa Area | Warehouse_IndustrialPool/Spa Area | 3438 | 0.65 | 0.64 | 0.4
|  |  | Warehouse_Industrial | Police/Fire Station | Warehouse_IndustrialPolice/Fire Station | 3438 | 0.65 | 0.64 | 0.4
|  |  | Warehouse_Industrial | Religious Worship | Warehouse_IndustrialReligious Worship | 3438 | 0.65 | 0.64 | 0.4
|  |  | Warehouse_Industrial | Residential | Warehouse_IndustrialResidential | 3438 | 0.65 | 0.64 | 0.4
|  |  | Warehouse_Industrial | Restrooms | Warehouse_IndustrialRestrooms | 4213 | 0.53 | 0.53 | 0.47
|  |  | Warehouse_Industrial | Retail Sales/Showroom | Warehouse_IndustrialRetail Sales/Showroom | 6152 | 0.97 | 0.97 | 0.78
|  |  | Warehouse_Industrial | Smoking Lounge | Warehouse_IndustrialSmoking Lounge | 3438 | 0.65 | 0.64 | 0.4
|  |  | Warehouse_Industrial | Storage (Conditioned) | Warehouse_IndustrialStorage (Conditioned) | 4530 | 0.81 | 0.82 | 0.4
|  |  | Warehouse_Industrial | Storage (Unconditioned) | Warehouse_IndustrialStorage (Unconditioned) | 2930 | 0.66 | 0.64 | 0.4
|  |  | Warehouse_Industrial | Storage (Refrigerated/Freezer),Walk-in | Warehouse_IndustrialStorage (Refrigerated/Freezer),Walk-in | 3338 | 0.71 | 0.69 | 0.44
|  |  | Warehouse_Industrial | Storage (Refrigerated/Freezer),Building | Warehouse_IndustrialStorage (Refrigerated/Freezer),Building | 3438 | 0.65 | 0.64 | 0.4
|  |  | Warehouse_Industrial | Surgery Rooms | Warehouse_IndustrialSurgery Rooms | 3438 | 0.65 | 0.64 | 0.4
|  |  | Warehouse_Industrial | Theater (Motion Picture) | Warehouse_IndustrialTheater (Motion Picture) | 3438 | 0.65 | 0.64 | 0.4
|  |  | Warehouse_Industrial | Theater (Performance) | Warehouse_IndustrialTheater (Performance) | 3438 | 0.65 | 0.64 | 0.4
|  |  | Warehouse_Industrial | Unknown | Warehouse_IndustrialUnknown | 3438 | 0.65 | 0.64 | 0.4
|  |  | Warehouse_Industrial | Vacant (Condtioned) | Warehouse_IndustrialVacant (Condtioned) | 3338 | 0.71 | 0.69 | 0.44
|  |  | Warehouse_Industrial | Vacant (Unconditioned) | Warehouse_IndustrialVacant (Unconditioned) | 3438 | 0.65 | 0.64 | 0.4
|  |  | Warehouse_Industrial | Vocational Areas | Warehouse_IndustrialVocational Areas | 3438 | 0.65 | 0.64 | 0.4
|  |  | Warehouse_Industrial | Parking Garage | Warehouse_IndustrialParking Garage | 8678 | 0.98 | 0.98 | 0.99
|  |  | Warehouse_Industrial | Non Rebated Area | Warehouse_IndustrialNon Rebated Area | 3438 | 0.65 | 0.64 | 0.4
|  |  | Warehouse_Industrial | Other Unlisted Activity Types | Warehouse_IndustrialOther Unlisted Activity Types | 3338 | 0.71 | 0.69 | 0.44
|  |  | Warehouse_Industrial | Outside/Outdoor Area | Warehouse_IndustrialOutside/Outdoor Area | 3604 | 0.11 | 0.11 | 0.58
|  |  | Other | Auditorium/Gym | OtherAuditorium/Gym | 3438 | 0.65 | 0.64 | 0.4
|  |  | Other | Auto Repair Workshop | OtherAuto Repair Workshop | 6189 | 0.88 | 0.89 | 0.61
|  |  | Other | Bank/Financial | OtherBank/Financial | 3438 | 0.65 | 0.64 | 0.4
|  |  | Other | Bar Cocktail Lounge | OtherBar Cocktail Lounge | 3438 | 0.65 | 0.64 | 0.4
|  |  | Other | Barber/Beauty Shop | OtherBarber/Beauty Shop | 3438 | 0.65 | 0.64 | 0.4
|  |  | Other | Casino/Gaming | OtherCasino/Gaming | 3438 | 0.65 | 0.64 | 0.4
|  |  | Other | Classroom/Lecture | OtherClassroom/Lecture | 1584 | 0.24 | 0.24 | 0.2
|  |  | Other | Clean Room | OtherClean Room | 3438 | 0.65 | 0.64 | 0.4
|  |  | Other | Computer Room/Data Processing | OtherComputer Room/Data Processing | 3438 | 0.65 | 0.64 | 0.4
|  |  | Other | Comm/Ind Work(General High Bay flr-to-clng ht >= 25ft) | OtherComm/Ind Work(General High Bay flr-to-clng ht >= 25ft) | 4790 | 0.9 | 0.91 | 0.82
|  |  | Other | Comm/Ind Work(General Low Bay flr-to-clng ht < 25ft) | OtherComm/Ind Work(General Low Bay flr-to-clng ht < 25ft) | 6775 | 0.95 | 0.95 | 0.77
|  |  | Other | Comm/Ind Work (Precision) | OtherComm/Ind Work (Precision) | 3438 | 0.65 | 0.64 | 0.4
|  |  | Other | Conference Room | OtherConference Room | 1201 | 0.28 | 0.3 | 0.16
|  |  | Other | Convention and Meeting Center | OtherConvention and Meeting Center | 3438 | 0.65 | 0.64 | 0.4
|  |  | Other | Copy Room | OtherCopy Room | 3438 | 0.65 | 0.64 | 0.4
|  |  | Other | Corridor/Hallways | OtherCorridor/Hallways | 5670 | 0.86 | 0.86 | 0.73
|  |  | Other | Courtrooms | OtherCourtrooms | 3438 | 0.65 | 0.64 | 0.4
|  |  | Other | Dining Area | OtherDining Area | 2962 | 0.48 | 0.53 | 0.51
|  |  | Other | Dry Cleaning | OtherDry Cleaning | 3438 | 0.65 | 0.64 | 0.4
|  |  | Other | Exercise Centers/Gymnasium | OtherExercise Centers/Gymnasium | 4833 | 0.81 | 0.82 | 0.6
|  |  | Other | Exhibit Display Area/Museum | OtherExhibit Display Area/Museum | 3438 | 0.65 | 0.64 | 0.4
|  |  | Other | Guest Room (Hotel/Motel) | OtherGuest Room (Hotel/Motel) | 3438 | 0.65 | 0.64 | 0.4
|  |  | Other | Kitchen/Break room & Food Prep | OtherKitchen/Break room & Food Prep | 3522 | 0.79 | 0.74 | 0.42
|  |  | Other | Laboratory | OtherLaboratory | 3438 | 0.65 | 0.64 | 0.4
|  |  | Other | Laundry | OtherLaundry | 3438 | 0.65 | 0.64 | 0.4
|  |  | Other | Library | OtherLibrary | 1957 | 0.44 | 0.46 | 0.31
|  |  | Other | Loading Dock | OtherLoading Dock | 7358 | 0.97 | 0.97 | 0.62
|  |  | Other | Lobby (Hotel) | OtherLobby (Hotel) | 3438 | 0.65 | 0.64 | 0.4
|  |  | Other | Lobby (Main Entry and Assembly) | OtherLobby (Main Entry and Assembly) | 5947 | 0.83 | 0.82 | 0.71
|  |  | Other | Lobby (Office Reception/Waiting) | OtherLobby (Office Reception/Waiting) | 3425 | 0.84 | 0.87 | 0.49
|  |  | Other | Locker and Dressing Room | OtherLocker and Dressing Room | 3438 | 0.65 | 0.64 | 0.4
|  |  | Other | Mall Arcade and Atrium | OtherMall Arcade and Atrium | 3438 | 0.65 | 0.64 | 0.4
|  |  | Other | Mechanical/Electrical Room | OtherMechanical/Electrical Room | 5026 | 0.73 | 0.74 | 0.46
|  |  | Other | Medical Offices and Exam rooms | OtherMedical Offices and Exam rooms | 3438 | 0.65 | 0.64 | 0.4
|  |  | Other | Office (Executive/Private) | OtherOffice (Executive/Private) | 1753 | 0.42 | 0.44 | 0.2
|  |  | Other | Office (General) | OtherOffice (General) | 3001 | 0.67 | 0.67 | 0.43
|  |  | Other | Office(Open Plan) | OtherOffice(Open Plan) | 3159 | 0.81 | 0.82 | 0.49
|  |  | Other | Patient Rooms | OtherPatient Rooms | 3438 | 0.65 | 0.64 | 0.4
|  |  | Other | Patio Area | OtherPatio Area | 3438 | 0.65 | 0.64 | 0.4
|  |  | Other | Pool/Spa Area | OtherPool/Spa Area | 3438 | 0.65 | 0.64 | 0.4
|  |  | Other | Police/Fire Station | OtherPolice/Fire Station | 3438 | 0.65 | 0.64 | 0.4
|  |  | Other | Religious Worship | OtherReligious Worship | 3438 | 0.65 | 0.64 | 0.4
|  |  | Other | Residential | OtherResidential | 3438 | 0.65 | 0.64 | 0.4
|  |  | Other | Restrooms | OtherRestrooms | 2521 | 0.48 | 0.42 | 0.3
|  |  | Other | Retail Sales/Showroom | OtherRetail Sales/Showroom | 6152 | 0.97 | 0.97 | 0.78
|  |  | Other | Smoking Lounge | OtherSmoking Lounge | 3438 | 0.65 | 0.64 | 0.4
|  |  | Other | Storage (Conditioned) | OtherStorage (Conditioned) | 4672 | 0.81 | 0.81 | 0.44
|  |  | Other | Storage (Unconditioned) | OtherStorage (Unconditioned) | 2930 | 0.66 | 0.64 | 0.4
|  |  | Other | Storage (Refrigerated/Freezer),Walk-in | OtherStorage (Refrigerated/Freezer),Walk-in | 4672 | 0.81 | 0.81 | 0.44
|  |  | Other | Storage (Refrigerated/Freezer),Building | OtherStorage (Refrigerated/Freezer),Building | 3438 | 0.65 | 0.64 | 0.4
|  |  | Other | Surgery Rooms | OtherSurgery Rooms | 3438 | 0.65 | 0.64 | 0.4
|  |  | Other | Theater (Motion Picture) | OtherTheater (Motion Picture) | 3438 | 0.65 | 0.64 | 0.4
|  |  | Other | Theater (Performance) | OtherTheater (Performance) | 3438 | 0.65 | 0.64 | 0.4
|  |  | Other | Unknown | OtherUnknown | 3438 | 0.65 | 0.64 | 0.4
|  |  | Other | Vacant (Condtioned) | OtherVacant (Condtioned) | 3438 | 0.65 | 0.64 | 0.4
|  |  | Other | Vacant (Unconditioned) | OtherVacant (Unconditioned) | 3438 | 0.65 | 0.64 | 0.4
|  |  | Other | Vocational Areas | OtherVocational Areas | 3438 | 0.65 | 0.64 | 0.4
|  |  | Other | Parking Garage | OtherParking Garage | 8678 | 0.98 | 0.98 | 0.99
|  |  | Other | Non Rebated Area | OtherNon Rebated Area | 3438 | 0.65 | 0.64 | 0.4
|  |  | Other | Other Unlisted Activity Types | OtherOther Unlisted Activity Types | 3438 | 0.65 | 0.64 | 0.4
|  |  | Other | Outside/Outdoor Area | OtherOutside/Outdoor Area | 3604 | 0.11 | 0.11 | 0.58

## Fixture Codes
FIXTURE SEARCH
Use drop-down arrows in each column heading to filter by parameter. If your application contains custom fixtures, the fixtures will need to be configured starting on row 919.
Fixture Code* | Lighting Category | Subcategory | Lamp Code | Description | Ballast | Ballasts Per Fixture | Tube Length | Lamps Per Fixture | Watts Per Lamp | Watts Per Fixture* | Baseline Fixture | CFLs_and_Custom | Exit_Signs_and_Custom | HIDs_and_Custom | Incandescents_and_Custom | LEDs_and_Custom | Lighting Category
CCFC1.5/1 | CFL | Cold Cathode CFL | CCFC1.5 | Cold-Cathode Compact Fluorescent, Screw-in, (1) 1.5W lamp | Electronic | 1 |  | 1 | 1.5 | 1.5 | CCFC1.5/1 | CCFC1.5/1 | ECF5/1 | HPS100/1 | H100/1 | SLED10/1 | CFL
CCFC3/1 | CFL | Cold Cathode CFL | CCFC3 | Cold-Cathode Compact Fluorescent, Screw-in, (1) 3W lamp | Electronic | 1 |  | 1 | 3 | 3 | CCFC3/1 | CCFC3/1 | ECF5/2 | HPS1000/1 | H1000/1 | SLED11/1 | Exit Sign
CCFC5/1 | CFL | Cold Cathode CFL | CCFC5 | Cold-Cathode Compact Fluorescent, Screw-in, (1) 5W lamp | Electronic | 1 |  | 1 | 5 | 5 | CCFC5/1 | CCFC5/1 | ECF7/1 | HPS150/1 | H1200/1 | SLED12/1 | High Intensity Discharge
CCFC8/1 | CFL | Cold Cathode CFL | CCFC8 | Cold-Cathode Compact Fluorescent, Screw-in, (1) 8W lamp | Electronic | 1 |  | 1 | 8 | 8 | CCFC8/1 | CCFC8/1 | ECF7/2 | HPS200/1 | H150/1 | SLED13/1 | Incandescent
CF10/2D | CFL | CFL Fixture | CFD10W | Compact Fluorescent, 2D, (1) 10W lamp | Mag-STD | 1 |  | 1 | 10 | 16 | CF10/2D | CF10/2D | ECF8/1 | HPS225/1 | H150/2 | SLED14/1 | LED
CF10/2D-L | CFL | CFL Fixture | CFD10W | Compact Fluorescent, 2D, (1) 10W lamp | Electronic | 1 |  | 1 | 10 | 12 | CF10/2D-L | CF10/2D-L | ECF8/2 | HPS250/1 | H1500/1 | SLED15/1 | Circular Fluorescent
CF11/1 | CFL | CFL Fixture | CF11W | Compact Fluorescent, (1) 11W lamp | Mag-STD | 1 |  | 1 | 11 | 13 | CF11/1 | CF11/1 | ECF9/1 | HPS310/1 | H200/1 | SLED16/1 | Linear Fluorescent
CF11/2 | CFL | CFL Fixture | CF11W | Compact Fluorescent, (2) 11W lamp | Mag-STD | 1 |  | 2 | 11 | 26 | CF11/2 | CF11/2 | ECF9/2 | HPS35/1 | H250/1 | SLED17/1 | U-Tube Fluorescent
CF16/2D | CFL | CFL Fixture | CFD16W | Compact Fluorescent, 2D, (1) 16W lamp | Mag-STD | 1 |  | 1 | 16 | 26 | CF16/2D | CF16/2D | EI10/2 | HPS360/1 | H300/1 | SLED18/1 | Induction Fluorescent
CF16/2D-L | CFL | CFL Fixture | CFD16W | Compact Fluorescent, 2D, (1) 16W lamp | Electronic | 1 |  | 1 | 16 | 18 | CF16/2D-L | CF16/2D-L | EI15/1 | HPS400/1 | H35/1 | SLED19/1
CF18/3-L | CFL | CFL Fixture | CF18W | Compact Fluorescent, (3) 18W lamp | Electronic | 1 |  | 3 | 18 | 60 | CF18/3-L | CF18/3-L | EI15/2 | HPS50/1 | H350/1 | SLED2/1
CF21/2D | CFL | CFL Fixture | CFD21W | Compact Fluorescent, 2D, (1) 21W lamp | Mag-STD | 1 |  | 1 | 21 | 26 | CF21/2D | CF21/2D | EI20/1 | HPS600/1 | H40/1 | SLED20/1
CF21/2D-L | CFL | CFL Fixture | CFD21W | Compact Fluorescent, 2D, (1) 21W lamp | Electronic | 1 |  | 1 | 21 | 22 | CF21/2D-L | CF21/2D-L | EI20/2 | HPS70/1 | H400/1 | SLED21/1
CF23/1 | CFL | CFL Fixture | CF23W | Compact Fluorescent, (1) 23W lamp | Mag-STD | 1 |  | 1 | 23 | 29 | CF23/1 | CF23/1 | EI25/1 | HPS750/1 | H42/1 | SLED22/1
CF23/1-L | CFL | CFL Fixture | CF23W | Compact Fluorescent, (1) 23W lamp | Electronic | 1 |  | 1 | 23 | 25 | CF23/1-L | CF23/1-L | EI25/2 | MH100/1 | H425/1 | SLED26/1
CF26/3-L | CFL | CFL Fixture | CF26W | Compact Fluorescent, (3) 26W lamp | Electronic | 1 |  | 3 | 26 | 82 | CF26/3-L | CF26/3-L | EI34/1 | MH1000/1 | H45/1 | SLED3/1
CF26/4-L | CFL | CFL Fixture | CF26W | Compact Fluorescent, (4) 26W lamp | Electronic | 1 |  | 4 | 26 | 108 | CF26/4-L | CF26/4-L | EI34/2 | MH150/1 | H45/2 | SLED4/1
CF26/6-L | CFL | CFL Fixture | CF26W | Compact Fluorescent, (6) 26W lamp | Electronic | 1 |  | 6 | 26 | 162 | CF26/6-L | CF26/6-L | EI40/1 | MH1500/1 | H50/1 | SLED5/1
CF26/8-L | CFL | CFL Fixture | CF26W | Compact Fluorescent, (8) 26W lamp | Electronic | 1 |  | 8 | 26 | 216 | CF26/8-L | CF26/8-L | EI40/2 | MH175/1 | H50/2 | SLED6/1
CF28/2D | CFL | CFL Fixture | CFD28W | Compact Fluorescent, 2D, (1) 28W lamp | Mag-STD | 1 |  | 1 | 28 | 35 | CF28/2D | CF28/2D | EI5/1 | MH1800/1 | H500/1 | SLED7/1
CF28/2D-L | CFL | CFL Fixture | CFD28W | Compact Fluorescent, 2D, (1) 28W lamp | Electronic | 1 |  | 1 | 28 | 28 | CF28/2D-L | CF28/2D-L | EI5/2 | MH200/1 | H52/1 | SLED8/1
CF32/3-L | CFL | CFL Fixture | CF32W | Compact Fluorescent, (3) 32W lamp | Electronic | 1 |  | 3 | 32 | 114 | CF32/3-L | CF32/3-L | EI50/2 | MH250/1 | H55/1 | SLED9/1
CF32/4-L | CFL | CFL Fixture | CF32W | Compact Fluorescent, (4) 32W lamp | Electronic | 1 |  | 4 | 32 | 152 | CF32/4-L | CF32/4-L | EI7.5/1 | MH300/1 | H55/2 | Enter Custom Fixture
CF32/6-L | CFL | CFL Fixture | CF32W | Compact Fluorescent, (6) 32W lamp | Electronic | 1 |  | 6 | 32 | 228 | CF32/6-L | CF32/6-L | EI7.5/2 | MH32/1 | H60/1 | Enter Custom Fixture
CF32/8-L | CFL | CFL Fixture | CF32W | Compact Fluorescent, (8) 32W lamp | Electronic | 1 |  | 8 | 32 | 304 | CF32/8-L | CF32/8-L | ELED0.5/1 | MH320/1 | H72/1 | Enter Custom Fixture
CF38/2D | CFL | CFL Fixture | CFD38W | Compact Fluorescent, 2D, (1) 38W lamp | Mag-STD | 1 |  | 1 | 38 | 46 | CF38/2D | CF38/2D | ELED0.5/2 | MH35/1 | H75/1 | Enter Custom Fixture
CF38/2D-L | CFL | CFL Fixture | CFD38W | Compact Fluorescent, 2D, (1) 38W lamp | Electronic | 1 |  | 1 | 38 | 36 | CF38/2D-L | CF38/2D-L | ELED1.5/1 | MH350/1 | H75/2 | Enter Custom Fixture
CF42/1-L | CFL | CFL Fixture | CF42W | Compact Fluorescent, (1) 42W lamp | Electronic | 1 |  | 1 | 42 | 48 | CF42/1-L | CF42/1-L | ELED1.5/2 | MH360/1 | H750/1 | Enter Custom Fixture
CF42/2-L | CFL | CFL Fixture | CF42W | Compact Fluorescent, (2) 42W lamp | Electronic | 1 |  | 2 | 42 | 100 | CF42/2-L | CF42/2-L | ELED10.5/1 | MH400/1 | H90/1 | Enter Custom Fixture
CF42/3-L | CFL | CFL Fixture | CF42W | Compact Fluorescent, (3) 42W lamp | Electronic | 1 |  | 3 | 42 | 141 | CF42/3-L | CF42/3-L | ELED10.5/2 | MH400/2 | H90/2 | Enter Custom Fixture
CF42/4-L | CFL | CFL Fixture | CF42W | Compact Fluorescent, (4) 42W lamp | Electronic | 1 |  | 4 | 42 | 188 | CF42/4-L | CF42/4-L | ELED2/1 | MH450/1 | H900/1 | Enter Custom Fixture
CF42/6-L | CFL | CFL Fixture | CF42W | Compact Fluorescent, (6) 42W lamp | Electronic | 1 |  | 6 | 42 | 282 | CF42/6-L | CF42/6-L | ELED2/2 | MH50/1 | HLV20/1 | Enter Custom Fixture
CF42/8-L | CFL | CFL Fixture | CF42W | Compact Fluorescent, (8) 42W lamp | Electronic | 1 |  | 8 | 42 | 376 | CF42/8-L | CF42/8-L | ELED3/1 | MH70/1 | HLV25/1 | Enter Custom Fixture
CFC/14/1 | CFL | CFL Screw-In | CFC14 | Compact Fluorescent, Screw-in, (1) 14W lamp | Electronic | 1 |  | 1 | 14 | 14 | CFC/14/1 | CFC/14/1 | ELED3/2 | MH750/1 | HLV35/1 | Enter Custom Fixture
CFC11/1 | CFL | CFL Screw-In | CFC11 | Compact Fluorescent, Screw-in, (1) 11W lamp | Electronic | 1 |  | 1 | 11 | 11 | CFC11/1 | CFC11/1 | ELED5/1 | MHPS/LR/100/1 | HLV42/1 | Enter Custom Fixture
CFC12/1 | CFL | CFL Screw-In | CFC12 | Compact Fluorescent, Screw-in, (1) 12W lamp | Electronic | 1 |  | 1 | 12 | 12 | CFC12/1 | CFC12/1 | ELED5/2 | MHPS/LR/150/1 | HLV50/1 | Enter Custom Fixture
CFC13/1 | CFL | CFL Screw-In | CFC13 | Compact Fluorescent, Screw-in, (1) 13W lamp | Electronic | 1 |  | 1 | 13 | 13 | CFC13/1 | CFC13/1 | ELED8/1 | MHPS/LR/175/1 | HLV65/1 | Enter Custom Fixture
CFC15/1 | CFL | CFL Screw-In | CFC15 | Compact Fluorescent, Screw-in, (1) 15W lamp | Electronic | 1 |  | 1 | 15 | 15 | CFC15/1 | CFC15/1 | ELED8/2 | MHPS/LR/200/1 | HLV75/1 | Enter Custom Fixture
CFC16/1 | CFL | CFL Screw-In | CFC16 | Compact Fluorescent, Screw-in, (1) 16W lamp | Electronic | 1 |  | 1 | 16 | 16 | CFC16/1 | CFC16/1 | Enter Custom Fixture | MHPS/LR/250/1 | I100/1 | Enter Custom Fixture
CFC17/1 | CFL | CFL Screw-In | CFC17 | Compact Fluorescent, Screw-in, (1) 17W lamp | Electronic | 1 |  | 1 | 17 | 17 | CFC17/1 | CFC17/1 | Enter Custom Fixture | MHPS/LR/300/1 | I100/2 | Enter Custom Fixture
CFC18/1 | CFL | CFL Screw-In | CFC18 | Compact Fluorescent, Screw-in, (1) 18W lamp | Electronic | 1 |  | 1 | 18 | 18 | CFC18/1 | CFC18/1 | Enter Custom Fixture | MHPS/LR/320/1 | I100/3 | Enter Custom Fixture
CFC20/1 | CFL | CFL Screw-In | CFC20 | Compact Fluorescent, Screw-in, (1) 20W lamp | Electronic | 1 |  | 1 | 20 | 20 | CFC20/1 | CFC20/1 | Enter Custom Fixture | MHPS/LR/350/1 | I100/4 | Enter Custom Fixture
CFC23/1 | CFL | CFL Screw-In | CFC23 | Compact Fluorescent, Screw-in, (1) 23W lamp | Electronic | 1 |  | 1 | 23 | 23 | CFC23/1 | CFC23/1 | Enter Custom Fixture | MHPS/LR/400/1 | I100/5 | Enter Custom Fixture
CFC26/1 | CFL | CFL Screw-In | CFC26 | Compact Fluorescent, Screw-in, (1) 26W lamp | Electronic | 1 |  | 1 | 26 | 26 | CFC26/1 | CFC26/1 | Enter Custom Fixture | MHPS/LR/450/1 | I1000/1 | Enter Custom Fixture
CFC30/1 | CFL | CFL Screw-In | CFC30 | Compact Fluorescent, Screw-in, (1) 30W lamp | Electronic | 1 |  | 1 | 30 | 30 | CFC30/1 | CFC30/1 | Enter Custom Fixture | MHPS/LR/750/1 | I100E/1 | Enter Custom Fixture
CFC7/1 | CFL | CFL Screw-In | CFC7 | Compact Fluorescent, Screw-in, (1) 7W lamp | Electronic | 1 |  | 1 | 7 | 7 | CFC7/1 | CFC7/1 | Enter Custom Fixture | MHPS/SCWA/100/1 | I100EL/1 | Enter Custom Fixture
CFC9/1 | CFL | CFL Screw-In | CFC9 | Compact Fluorescent, Screw-in, (1) 9W lamp | Electronic | 1 |  | 1 | 9 | 9 | CFC9/1 | CFC9/1 | Enter Custom Fixture | MHPS/SCWA/1000/1 | I120/1 | Enter Custom Fixture
CFQ10/1 | CFL | CFL Fixture | CFQ10W | Compact Fluorescent, quad, (1) 10W lamp | Mag-STD | 1 |  | 1 | 10 | 15 | CFQ10/1 | CFQ10/1 | Enter Custom Fixture | MHPS/SCWA/150/1 | I120/2 | Enter Custom Fixture
CFQ13/1 | CFL | CFL Fixture | CFQ13W | Compact Fluorescent, quad, (1) 13W lamp | Mag-STD | 1 |  | 1 | 13 | 17 | CFQ13/1 | CFQ13/1 | Enter Custom Fixture | MHPS/SCWA/175/1 | I125/1 | Enter Custom Fixture
CFQ13/1-L | CFL | CFL Fixture | CFQ13W | Compact Fluorescent, quad, (1) 13W lamp, BF=1.05 | Electronic | 1 |  | 1 | 13 | 15 | CFQ13/1-L | CFQ13/1-L | Enter Custom Fixture | MHPS/SCWA/200/1 | I135/1 | Enter Custom Fixture
CFQ13/2 | CFL | CFL Fixture | CFQ13W | Compact Fluorescent, quad, (2) 13W lamp | Mag-STD | 1 |  | 2 | 13 | 31 | CFQ13/2 | CFQ13/2 | Enter Custom Fixture | MHPS/SCWA/250/1 | I135/2 | Enter Custom Fixture
CFQ13/2-L | CFL | CFL Fixture | CFQ13W | Compact Fluorescent, quad, (2) 13W lamp, BF=1.0 | Electronic | 1 |  | 2 | 13 | 28 | CFQ13/2-L | CFQ13/2-L | Enter Custom Fixture | MHPS/SCWA/300/1 | I15/1 | Enter Custom Fixture
CFQ13/3 | CFL | CFL Fixture | CFQ13W | Compact Fluorescent, quad, (3) 13W lamp | Mag-STD | 1 |  | 3 | 13 | 48 | CFQ13/3 | CFQ13/3 | Enter Custom Fixture | MHPS/SCWA/320/1 | I15/2 | Enter Custom Fixture
CFQ15/1 | CFL | CFL Fixture | CFQ15W | Compact Fluorescent, quad, (1) 15W lamp | Mag-STD | 1 |  | 1 | 15 | 20 | CFQ15/1 | CFQ15/1 | Enter Custom Fixture | MHPS/SCWA/350/1 | I150/1 | Enter Custom Fixture
CFQ17/1 | CFL | CFL Fixture | CFQ17W | Compact Fluorescent, quad, (1) 17W lamp | Mag-STD | 1 |  | 1 | 17 | 24 | CFQ17/1 | CFQ17/1 | Enter Custom Fixture | MHPS/SCWA/400/1 | I150/2 | Enter Custom Fixture
CFQ17/2 | CFL | CFL Fixture | CFQ17W | Compact Fluorescent, quad, (2) 17W lamp | Mag-STD | 1 |  | 2 | 17 | 48 | CFQ17/2 | CFQ17/2 | Enter Custom Fixture | MHPS/SCWA/450/1 | I1500/1 | Enter Custom Fixture
CFQ18/1 | CFL | CFL Fixture | CFQ18W | Compact Fluorescent, quad, (1) 18W lamp | Mag-STD | 1 |  | 1 | 18 | 26 | CFQ18/1 | CFQ18/1 | Enter Custom Fixture | MHPS/SCWA/750/1 | I150E/1 | Enter Custom Fixture
CFQ18/1-L | CFL | CFL Fixture | CFQ18W | Compact Fluorescent, quad, (1) 18W lamp, BF=1.0 | Electronic | 1 |  | 1 | 18 | 20 | CFQ18/1-L | CFQ18/1-L | Enter Custom Fixture | MV100/1 | I150EL/1 | Enter Custom Fixture
CFQ18/2 | CFL | CFL Fixture | CFQ18W | Compact Fluorescent, quad, (2) 18W lamp | Mag-STD | 1 |  | 2 | 18 | 45 | CFQ18/2 | CFQ18/2 | Enter Custom Fixture | MV1000/1 | I170/1 | Enter Custom Fixture
CFQ18/2-L | CFL | CFL Fixture | CFQ18W | Compact Fluorescent, quad, (2) 18W lamp, BF=1.0 | Electronic | 1 |  | 2 | 18 | 38 | CFQ18/2-L | CFQ18/2-L | Enter Custom Fixture | MV175/1 | I20/1 | Enter Custom Fixture
CFQ18/4 | CFL | CFL Fixture | CFQ18W | Compact Fluorescent, quad, (4) 18W lamp | Mag-STD | 1 |  | 4 | 18 | 90 | CFQ18/4 | CFQ18/4 | Enter Custom Fixture | MV250/1 | I20/2 | Enter Custom Fixture
CFQ20/1 | CFL | CFL Fixture | CFQ20W | Compact Fluorescent, quad, (1) 20W lamp | Mag-STD | 1 |  | 1 | 20 | 23 | CFQ20/1 | CFQ20/1 | Enter Custom Fixture | MV40/1 | I200/1 | Enter Custom Fixture
CFQ20/2 | CFL | CFL Fixture | CFQ20W | Compact Fluorescent, quad, (2) 20W lamp | Mag-STD | 1 |  | 2 | 20 | 46 | CFQ20/2 | CFQ20/2 | Enter Custom Fixture | MV400/1 | I200/2 | Enter Custom Fixture
CFQ22/1 | CFL | CFL Fixture | CFQ22W | Compact Fluorescent, quad, (1) 22W lamp | Mag-STD | 1 |  | 1 | 22 | 24 | CFQ22/1 | CFQ22/1 | Enter Custom Fixture | MV400/2 | I2000/1 | Enter Custom Fixture
CFQ22/2 | CFL | CFL Fixture | CFQ22W | Compact Fluorescent, quad, (2) 22W lamp | Mag-STD | 1 |  | 2 | 22 | 48 | CFQ22/2 | CFQ22/2 | Enter Custom Fixture | MV50/1 | I200L/1 | Enter Custom Fixture
CFQ22/3 | CFL | CFL Fixture | CFQ22W | Compact Fluorescent, quad, (3) 22W lamp | Mag-STD | 1 |  | 3 | 22 | 72 | CFQ22/3 | CFQ22/3 | Enter Custom Fixture | MV700/1 | I25/1 | Enter Custom Fixture
CFQ25/1 | CFL | CFL Fixture | CFQ25W | Compact Fluorescent, quad, (1) 25W lamp | Mag-STD | 1 |  | 1 | 25 | 33 | CFQ25/1 | CFQ25/1 | Enter Custom Fixture | MV75/1 | I25/2 | Enter Custom Fixture
CFQ25/2 | CFL | CFL Fixture | CFQ25W | Compact Fluorescent, quad, (2) 25W lamp | Mag-STD | 1 |  | 2 | 25 | 66 | CFQ25/2 | CFQ25/2 | Enter Custom Fixture | Enter Custom Fixture | I25/4 | Enter Custom Fixture
CFQ26/1 | CFL | CFL Fixture | CFQ26W | Compact Fluorescent, quad, (1) 26W lamp | Mag-STD | 1 |  | 1 | 26 | 33 | CFQ26/1 | CFQ26/1 | Enter Custom Fixture | Enter Custom Fixture | I250/1 | Enter Custom Fixture
CFQ26/1-L | CFL | CFL Fixture | CFQ26W | Compact Fluorescent, quad, (1) 26W lamp, BF=0.95 | Electronic | 1 |  | 1 | 26 | 27 | CFQ26/1-L | CFQ26/1-L | Enter Custom Fixture | Enter Custom Fixture | I300/1 | Enter Custom Fixture
CFQ26/2 | CFL | CFL Fixture | CFQ26W | Compact Fluorescent, quad, (2) 26W lamp | Mag-STD | 1 |  | 2 | 26 | 66 | CFQ26/2 | CFQ26/2 | Enter Custom Fixture | Enter Custom Fixture | I34/1 | Enter Custom Fixture
CFQ26/2-L | CFL | CFL Fixture | CFQ26W | Compact Fluorescent, quad, (2) 26W lamp, BF=0.95 | Electronic | 1 |  | 2 | 26 | 50 | CFQ26/2-L | CFQ26/2-L | Enter Custom Fixture | Enter Custom Fixture | I34/2 | Enter Custom Fixture
CFQ26/3 | CFL | CFL Fixture | CFQ26W | Compact Fluorescent, quad, (3) 26W lamp | Mag-STD | 1 |  | 3 | 26 | 99 | CFQ26/3 | CFQ26/3 | Enter Custom Fixture | Enter Custom Fixture | I36/1 | Enter Custom Fixture
CFQ26/6-L | CFL | CFL Fixture | CFQ26W | Compact Fluorescent, quad, (6) 26W lamp, BF=0.95 | Electronic | 1 |  | 6 | 26 | 150 | CFQ26/6-L | CFQ26/6-L | Enter Custom Fixture | Enter Custom Fixture | I40/1 | Enter Custom Fixture
CFQ28/1 | CFL | CFL Fixture | CFQ28W | Compact Fluorescent, quad, (1) 28W lamp | Mag-STD | 1 |  | 1 | 28 | 33 | CFQ28/1 | CFQ28/1 | Enter Custom Fixture | Enter Custom Fixture | I40/2 | Enter Custom Fixture
CFQ9/1 | CFL | CFL Fixture | CFQ9W | Compact Fluorescent, quad, (1) 9W lamp | Mag-STD | 1 |  | 1 | 9 | 14 | CFQ9/1 | CFQ9/1 | Enter Custom Fixture | Enter Custom Fixture | I400/1 | Enter Custom Fixture
CFQ9/2 | CFL | CFL Fixture | CFQ9W | Compact Fluorescent, quad, (2) 9W lamp | Mag-STD | 1 |  | 2 | 9 | 23 | CFQ9/2 | CFQ9/2 | Enter Custom Fixture | Enter Custom Fixture | I40E/1 | Enter Custom Fixture
CFS11/1 | CFL | CFL Fixture | CFS11W | Compact Fluorescent, spiral, (1) 11W lamp | Electronic | 1 |  | 1 | 11 | 11 | CFS11/1 | CFS11/1 | Enter Custom Fixture | Enter Custom Fixture | I40EL/1 | Enter Custom Fixture
CFS13/1 | CFL | CFL Fixture | CFS13W | Compact Fluorescent, spiral, (1) 13W lamp | Electronic | 1 |  | 1 | 13 | 13 | CFS13/1 | CFS13/1 | Enter Custom Fixture | Enter Custom Fixture | I42/1 | Enter Custom Fixture
CFS15/1 | CFL | CFL Fixture | CFS15W | Compact Fluorescent, spiral, (1) 15W lamp | Electronic | 1 |  | 1 | 15 | 15 | CFS15/1 | CFS15/1 | Enter Custom Fixture | Enter Custom Fixture | I448/1 | Enter Custom Fixture
CFS20/1 | CFL | CFL Fixture | CFS20W | Compact Fluorescent, spiral, (1) 20W lamp | Electronic | 1 |  | 1 | 20 | 20 | CFS20/1 | CFS20/1 | Enter Custom Fixture | Enter Custom Fixture | I45/1
CFS23/1 | CFL | CFL Fixture | CFS23W | Compact Fluorescent, spiral, (1) 23W lamp | Electronic | 1 |  | 1 | 23 | 23 | CFS23/1 | CFS23/1 | Enter Custom Fixture | Enter Custom Fixture | I50/1
CFS26/1 | CFL | CFL Fixture | CFS26W | Compact Fluorescent, spiral, (1) 26W lamp | Electronic | 1 |  | 1 | 26 | 26 | CFS26/1 | CFS26/1 | Enter Custom Fixture | Enter Custom Fixture | I50/2
CFS27/1 | CFL | CFL Fixture | CFS27W | Compact Fluorescent, spiral, (1) 27W lamp | Electronic | 1 |  | 1 | 27 | 27 | CFS27/1 | CFS27/1 | Enter Custom Fixture | Enter Custom Fixture | I500/1
CFS7/1 | CFL | CFL Fixture | CFS7W | Compact Fluorescent, spiral, (1) 7W lamp | Electronic | 1 |  | 1 | 7 | 7 | CFS7/1 | CFS7/1 | Enter Custom Fixture | Enter Custom Fixture | I52/1
CFS9/1 | CFL | CFL Fixture | CFS9W | Compact Fluorescent, spiral, (1) 9W lamp | Electronic | 1 |  | 1 | 9 | 9 | CFS9/1 | CFS9/1 | Enter Custom Fixture | Enter Custom Fixture | I52/2
CFT05/1 | CFL | CFL Fixture | CFT5W | Compact Fluorescent, twin, (1) 5W lamp | Mag-STD | 1 |  | 1 | 5 | 9 | CFT5/1 | CFT05/1 | Enter Custom Fixture | Enter Custom Fixture | I54/1
CFT13/1 | CFL | CFL Fixture | CFT13W | Compact Fluorescent, twin, (1) 13W lamp | Mag-STD | 1 |  | 1 | 13 | 17 | CFT13/1 | CFT13/1 | Enter Custom Fixture | Enter Custom Fixture | I54/2
CFT13/2 | CFL | CFL Fixture | CFT13W | Compact Fluorescent, twin, (2) 13W lamp | Mag-STD | 1 |  | 2 | 13 | 31 | CFT13/2 | CFT13/2 | Enter Custom Fixture | Enter Custom Fixture | I55/1
CFT13/3 | CFL | CFL Fixture | CFT13W | Compact Fluorescent, twin, (3) 13 W lamp | Mag-STD | 1 |  | 3 | 13 | 48 | CFT13/3 | CFT13/3 | Enter Custom Fixture | Enter Custom Fixture | I55/2
CFT18/1 | CFL | CFL Fixture | CFT18W | Compact Fluorescent, long twin., (1) 18W lamp | Mag-STD | 1 |  | 1 | 18 | 24 | CFT18/1 | CFT18/1 | Enter Custom Fixture | Enter Custom Fixture | I60/1
CFT22/1 | CFL | CFL Fixture | CFT22W | Compact Fluorescent, twin, (1) 22W lamp | Mag-STD | 1 |  | 1 | 22 | 27 | CFT22/1 | CFT22/1 | Enter Custom Fixture | Enter Custom Fixture | I60/2
CFT22/2 | CFL | CFL Fixture | CFT22W | Compact Fluorescent, twin, (2) 22W lamp | Mag-STD | 1 |  | 2 | 22 | 54 | CFT22/2 | CFT22/2 | Enter Custom Fixture | Enter Custom Fixture | I60/3
CFT22/4 | CFL | CFL Fixture | CFT22W | Compact Fluorescent, twin, (4) 22W lamp | Mag-STD | 1 |  | 4 | 22 | 108 | CFT22/4 | CFT22/4 | Enter Custom Fixture | Enter Custom Fixture | I60/4
CFT24/1 | CFL | CFL Fixture | CFT24W | Compact Fluorescent, long twin, (1) 24W lamp | Mag-STD | 1 |  | 1 | 24 | 32 | CFT24/1 | CFT24/1 | Enter Custom Fixture | Enter Custom Fixture | I60/5
CFT28/1 | CFL | CFL Fixture | CFT28W | Compact Fluorescent, twin, (1) 28W lamp | Mag-STD | 1 |  | 1 | 28 | 33 | CFT28/1 | CFT28/1 | Enter Custom Fixture | Enter Custom Fixture | I60E/1
CFT28/2 | CFL | CFL Fixture | CFT28W | Compact Fluorescent, twin, (2) 28W lamp | Mag-STD | 1 |  | 2 | 28 | 66 | CFT28/2 | CFT28/2 |  | Enter Custom Fixture | I60EL/1
CFT32/1-L | CFL | CFL Fixture | CFM32W | Compact Fluorescent, twin or multi, (1) 32W lamp | Electronic | 1 |  | 1 | 32 | 34 | CFT32/1-L | CFT32/1-L |  | Enter Custom Fixture | I65/1
CFT32/2-L | CFL | CFL Fixture | CFM32W | Compact Fluorescent, twin or multi, (2) 32W lamp | Electronic | 1 |  | 2 | 32 | 62 | CFT32/2-L | CFT32/2-L |  | Enter Custom Fixture | I65/2
CFT32/6-L | CFL | CFL Fixture | CFM32W | Compact Fluorescent, twin or multi, (6) 32W lamp | Electronic | 1 |  | 6 | 32 | 186 | CFT32/6-L | CFT32/6-L |  | Enter Custom Fixture | I67/1
CFT36/1 | CFL | CFL Fixture | CFT36W | Compact Fluorescent, long twin, (1) 36W lamp | Mag-STD | 1 |  | 1 | 36 | 51 | CFT36/1 | CFT36/1 |  | Enter Custom Fixture | I67/2
CFT36/4-BX | CFL | CFL Fixture | CFT36W | Compact Fluorescent, Biax, (4) 36W lamp | Electronic | 1 |  | 4 | 36 | 148 | CFT36/4-BX | CFT36/4-BX |  | Enter Custom Fixture | I67/3
CFT36/6-BX | CFL | CFL Fixture | CFT36W | Compact Fluorescent, Biax, (6) 36W lamp | Electronic | 1 |  | 6 | 36 | 212 | CFT36/6-BX | CFT36/6-BX |  | Enter Custom Fixture | I69/1
CFT36/6-L | CFL | CFL Fixture | CFT36W | Compact Fluorescent, long Twin, (6) 36W lamp | Electronic | 1 |  | 6 | 36 | 198 | CFT36/6-L | CFT36/6-L |  | Enter Custom Fixture | I7.5/1
CFT36/6-LH | CFL | CFL Fixture | CFT36W | Compact Fluorescent, long Twin, (6) 36W lamp/ High Ballast Factor | Electronic | 1 |  | 6 | 36 | 210 | CFT36/6-LH | CFT36/6-LH |  | Enter Custom Fixture | I7.5/2
CFT36/8-BX | CFL | CFL Fixture | CFT36W | Compact Fluorescent, Biax, (8) 36W lamp | Electronic | 1 |  | 8 | 36 | 296 | CFT36/8-BX | CFT36/8-BX |  | Enter Custom Fixture | I72/1
CFT36/8-L | CFL | CFL Fixture | CFT36W | Compact Fluorescent, long Twin, (8) 36W lamp | Electronic | 1 |  | 8 | 36 | 270 | CFT36/8-L | CFT36/8-L |  | Enter Custom Fixture | I75/1
CFT36/8-LH | CFL | CFL Fixture | CFT36W | Compact Fluorescent, long Twin, (8) 36W lamp/ High Ballast Factor | Electronic | 1 |  | 8 | 36 | 286 | CFT36/8-LH | CFT36/8-LH |  | Enter Custom Fixture | I75/2
CFT36/9-BX | CFL | CFL Fixture | CFT36W | Compact Fluorescent, Biax, (9) 36W lamp | Electronic | 1 |  | 9 | 36 | 318 | CFT36/9-BX | CFT36/9-BX |  | Enter Custom Fixture | I75/3
CFT40/1 | CFL | CFL Fixture | CFT40W | Compact Fluorescent, twin, (1) 40W lamp | Mag-STD | 1 |  | 1 | 40 | 46 | CFT40/1 | CFT40/1 |  | Enter Custom Fixture | I75/4
CFT40/12-BX | CFL | CFL Fixture | CFT40W | Compact Fluorescent, Biax, (12) 40W lamp | Electronic | 1 |  | 12 | 40 | 408 | CFT40/12-BX | CFT40/12-BX |  | Enter Custom Fixture | I750/1
CFT40/1-BX | CFL | CFL Fixture | CFT40W | Compact Fluorescent, Biax, (1) 40W lamp | Electronic | 1 |  | 1 | 40 | 46 | CFT40/1-BX | CFT40/1-BX |  | Enter Custom Fixture | I75E/1
CFT40/1-L | CFL | CFL Fixture | CFT40W | Compact Fluorescent, long twin, (1) 40W lamp | Electronic | 1 |  | 1 | 40 | 43 | CFT40/1-L | CFT40/1-L |  | Enter Custom Fixture | I75EL/1
CFT40/2 | CFL | CFL Fixture | CFT40W | Compact Fluorescent, twin, (2) 40W lamp | Mag-STD | 1 |  | 2 | 40 | 85 | CFT40/2 | CFT40/2 |  | Enter Custom Fixture | I80/1
CFT40/2-BX | CFL | CFL Fixture | CFT40W | Compact Fluorescent, Biax, (2) 40W lamp | Electronic | 1 |  | 2 | 40 | 72 | CFT40/2-BX | CFT40/2-BX |  | Enter Custom Fixture | I85/1
CFT40/2-L | CFL | CFL Fixture | CFT40W | Compact Fluorescent, long twin, (2) 40W lamp | Electronic | 1 |  | 2 | 40 | 72 | CFT40/2-L | CFT40/2-L |  | Enter Custom Fixture | I90/1
CFT40/3 | CFL | CFL Fixture | CFT40W | Compact Fluorescent, twin, (3) 40 W lamp | Mag-STD | 1 |  | 3 | 40 | 133 | CFT40/3 | CFT40/3 |  | Enter Custom Fixture | I90/2
CFT40/3-BX | CFL | CFL Fixture | CFT40W | Compact Fluorescent, Biax, (3) 40W lamp | Electronic | 1 |  | 3 | 40 | 102 | CFT40/3-BX | CFT40/3-BX |  | Enter Custom Fixture | I90/3
CFT40/3-L | CFL | CFL Fixture | CFT40W | Compact Fluorescent, long twin, (3) 40W lamp | Electronic | 1 |  | 3 | 40 | 105 | CFT40/3-L | CFT40/3-L |  | Enter Custom Fixture | I93/1
CFT40/4-BX | CFL | CFL Fixture | CFT40W | Compact Fluorescent, Biax, (4) 40W lamp | Electronic | 1 |  | 4 | 40 | 144 | CFT40/4-BX | CFT40/4-BX |  | Enter Custom Fixture | I95/1
CFT40/5-BX | CFL | CFL Fixture | CFT40W | Compact Fluorescent, Biax, (5) 40W lamp | Electronic | 1 |  | 5 | 40 | 190 | CFT40/5-BX | CFT40/5-BX |  | Enter Custom Fixture | I95/2
CFT40/6-BX | CFL | CFL Fixture | CFT40W | Compact Fluorescent, Biax, (6) 40W lamp | Electronic | 1 |  | 6 | 40 | 204 | CFT40/6-BX | CFT40/6-BX |  | Enter Custom Fixture | Enter Custom Fixture
CFT40/6-L | CFL | CFL Fixture | CFT40W | Compact Fluorescent, long Twin, (6) 40W lamp | Electronic | 1 |  | 6 | 40 | 220 | CFT40/6-L | CFT40/6-L |  | Enter Custom Fixture | Enter Custom Fixture
CFT40/6-LH | CFL | CFL Fixture | CFT40W | Compact Fluorescent, long Twin, (6) 40W lamp/ High Ballast Factor | Electronic | 1 |  | 6 | 40 | 233 | CFT40/6-LH | CFT40/6-LH |  | Enter Custom Fixture | Enter Custom Fixture
CFT40/8-BX | CFL | CFL Fixture | CFT40W | Compact Fluorescent, Biax, (8) 40W lamp | Electronic | 1 |  | 8 | 40 | 288 | CFT40/8-BX | CFT40/8-BX |  | Enter Custom Fixture | Enter Custom Fixture
CFT40/8-L | CFL | CFL Fixture | CFT40W | Compact Fluorescent, long Twin, (8) 40W lamp | Electronic | 1 |  | 8 | 40 | 300 | CFT40/8-L | CFT40/8-L |  |  | Enter Custom Fixture
CFT40/8-LH | CFL | CFL Fixture | CFT40W | Compact Fluorescent, long Twin, (8) 40W lamp/ High Ballast Factor | Electronic | 1 |  | 8 | 40 | 340 | CFT40/8-LH | CFT40/8-LH |  |  | Enter Custom Fixture
CFT40/9-BX | CFL | CFL Fixture | CFT40W | Compact Fluorescent, Biax, (9) 40W lamp | Electronic | 1 |  | 9 | 40 | 306 | CFT40/9-BX | CFT40/9-BX |  |  | Enter Custom Fixture
CFT5/2 | CFL | CFL Fixture | CFT5W | Compact Fluorescent, twin, (2) 5W lamp | Mag-STD | 1 |  | 2 | 5 | 18 | CFT5/2 | CFT5/2 |  |  | Enter Custom Fixture
CFT50/12-BX | CFL | CFL Fixture | CFT50W | Compact Fluorescent, Biax, (12) 50W lamp | Electronic | 1 |  | 12 | 50 | 648 | CFT50/12-BX | CFT50/12-BX |  |  | Enter Custom Fixture
CFT50/1-BX | CFL | CFL Fixture | CFT50W | Compact Fluorescent, Biax, (1) 50W lamp | Electronic | 1 |  | 1 | 50 | 54 | CFT50/1-BX | CFT50/1-BX |  |  | Enter Custom Fixture
CFT50/2-BX | CFL | CFL Fixture | CFT50W | Compact Fluorescent, Biax, (2) 50W lamp | Electronic | 1 |  | 2 | 50 | 108 | CFT50/2-BX | CFT50/2-BX |  |  | Enter Custom Fixture
CFT50/3-BX | CFL | CFL Fixture | CFT50W | Compact Fluorescent, Biax, (3) 50W lamp | Electronic | 1 |  | 3 | 50 | 162 | CFT50/3-BX | CFT50/3-BX |  |  | Enter Custom Fixture
CFT50/4-BX | CFL | CFL Fixture | CFT50W | Compact Fluorescent, Biax, (4) 50W lamp | Electronic | 1 |  | 4 | 50 | 216 | CFT50/4-BX | CFT50/4-BX |  |  | Enter Custom Fixture
CFT50/5-BX | CFL | CFL Fixture | CFT50W | Compact Fluorescent, Biax, (5) 50W lamp | Electronic | 1 |  | 5 | 50 | 270 | CFT50/5-BX | CFT50/5-BX |  |  | Enter Custom Fixture
CFT50/6-BX | CFL | CFL Fixture | CFT50W | Compact Fluorescent, Biax, (6) 50W lamp | Electronic | 1 |  | 6 | 50 | 324 | CFT50/6-BX | CFT50/6-BX |  |  | Enter Custom Fixture
CFT50/8-BX | CFL | CFL Fixture | CFT50W | Compact Fluorescent, Biax, (8) 50W lamp | Electronic | 1 |  | 8 | 50 | 432 | CFT50/8-BX | CFT50/8-BX |  |  | Enter Custom Fixture
CFT50/9-BX | CFL | CFL Fixture | CFT50W | Compact Fluorescent, Biax, (9) 50W lamp | Electronic | 1 |  | 9 | 50 | 486 | CFT50/9-BX | CFT50/9-BX |  |  | Enter Custom Fixture
CFT55/12-BX | CFL | CFL Fixture | CFT55W | Compact Fluorescent, Biax, (12) 55W lamp | Electronic | 1 |  | 12 | 55 | 672 | CFT55/12-BX | CFT55/12-BX |  |  | Enter Custom Fixture
CFT55/1-BX | CFL | CFL Fixture | CFT55W | Compact Fluorescent, Biax, (1) 55W lamp | Electronic | 1 |  | 1 | 55 | 56 | CFT55/1-BX | CFT55/1-BX |  |  | Enter Custom Fixture
CFT55/2-BX | CFL | CFL Fixture | CFT55W | Compact Fluorescent, Biax, (2) 55W lamp | Electronic | 1 |  | 2 | 55 | 112 | CFT55/2-BX | CFT55/2-BX |  |  | Enter Custom Fixture
CFT55/3-BX | CFL | CFL Fixture | CFT55W | Compact Fluorescent, Biax, (3) 55W lamp | Electronic | 1 |  | 3 | 55 | 168 | CFT55/3-BX | CFT55/3-BX |  |  | Enter Custom Fixture
CFT55/4-BX | CFL | CFL Fixture | CFT55W | Compact Fluorescent, Biax, (4) 55W lamp | Electronic | 1 |  | 4 | 55 | 224 | CFT55/4-BX | CFT55/4-BX |  |  | Enter Custom Fixture
CFT55/5-BX | CFL | CFL Fixture | CFT55W | Compact Fluorescent, Biax, (5) 55W lamp | Electronic | 1 |  | 5 | 55 | 280 | CFT55/5-BX | CFT55/5-BX |  |  | Enter Custom Fixture
CFT55/6-BX | CFL | CFL Fixture | CFT55W | Compact Fluorescent, Biax, (6) 55W lamp | Electronic | 1 |  | 6 | 55 | 336 | CFT55/6-BX | CFT55/6-BX |  |  | Enter Custom Fixture
CFT55/6-L | CFL | CFL Fixture | CFT55W | Compact Fluorescent, long Twin, (6) 55W lamp | Electronic | 1 |  | 6 | 55 | 352 | CFT55/6-L | CFT55/6-L |  |  | Enter Custom Fixture
CFT55/6-LH | CFL | CFL Fixture | CFT55W | Compact Fluorescent, long Twin, (6) 55W lamp/ High Ballast Factor | Electronic | 1 |  | 6 | 55 | 373 | CFT55/6-LH | CFT55/6-LH |  |  | Enter Custom Fixture
CFT55/8-BX | CFL | CFL Fixture | CFT55W | Compact Fluorescent, Biax, (8) 55W lamp | Electronic | 1 |  | 8 | 55 | 448 | CFT55/8-BX | CFT55/8-BX |  |  | Enter Custom Fixture
CFT55/8-L | CFL | CFL Fixture | CFT55W | Compact Fluorescent, long Twin, (8) 55W lamp | Electronic | 1 |  | 8 | 55 | 468 | CFT55/8-L | CFT55/8-L |  |  | Enter Custom Fixture
CFT55/8-LH | CFL | CFL Fixture | CFT55W | Compact Fluorescent, long Twin, (8) 55W lamp/ High Ballast Factor | Electronic | 1 |  | 8 | 55 | 496 | CFT55/8-LH | CFT55/8-LH |  |  | Enter Custom Fixture
CFT55/9-BX | CFL | CFL Fixture | CFT55W | Compact Fluorescent, Biax, (9) 55W lamp | Electronic | 1 |  | 9 | 55 | 504 | CFT55/9-BX | CFT55/9-BX |  |  | Enter Custom Fixture
CFT7/1 | CFL | CFL Fixture | CFT7W | Compact Fluorescent, twin, (1) 7W lamp | Mag-STD | 1 |  | 1 | 7 | 10 | CFT7/1 | CFT7/1 |  |  | Enter Custom Fixture
CFT7/2 | CFL | CFL Fixture | CFT7W | Compact Fluorescent, twin, (2) 7W lamp | Mag-STD | 1 |  | 2 | 7 | 21 | CFT7/2 | CFT7/2 |  |  | Enter Custom Fixture
CFT9/1 | CFL | CFL Fixture | CFT9W | Compact Fluorescent, twin, (1) 9W lamp | Mag-STD | 1 |  | 1 | 9 | 11 | CFT9/1 | CFT9/1 |  |  | Enter Custom Fixture
CFT9/2 | CFL | CFL Fixture | CFT9W | Compact Fluorescent, twin, (2) 9W lamp | Mag-STD | 1 |  | 2 | 9 | 23 | CFT9/2 | CFT9/2 |  |  | Enter Custom Fixture
CFT9/3 | CFL | CFL Fixture | CFT9W | Compact Fluorescent, twin, (3) 9W lamp | Mag-STD | 1 |  | 3 | 9 | 34 | CFT9/3 | CFT9/3 |  |  | Enter Custom Fixture
FC12/1 | Circular Fluorescent | Circular Fluorescent | FC12T9 | Fluorescent, (1) 12" circular lamp, RS ballast | Mag-STD | 1 | 12 | 1 | 32 | 31 | FC12/1 | Enter Custom Fixture |  |  | Enter Custom Fixture
FC12/2 | Circular Fluorescent | Circular Fluorescent | FC12T9 | Fluorescent, (2) 12" circular lamp, RS ballast | Mag-STD | 1 | 12 | 2 | 32 | 62 | FC12/2 | Enter Custom Fixture |  |  | Enter Custom Fixture
FC16/1 | Circular Fluorescent | Circular Fluorescent | FC16T9 | Fluorescent, (1) 16" circular lamp | Mag-STD | 1 | 16 | 1 | 40 | 35 | FC16/1 | Enter Custom Fixture |  |  | Enter Custom Fixture
FC20 | Circular Fluorescent | Circular Fluorescent | FC6T9 | Fluorescent, Circlite, (1) 20W lamp, Preheat ballast | Mag-STD | 1 |  | 1 | 20 | 20 | FC20 | Enter Custom Fixture |  |  | Enter Custom Fixture
FC22/1 | Circular Fluorescent | Circular Fluorescent | FC8T9 | Fluorescent, Circlite, (1) 22W lamp, preheat ballast | Mag-STD | 1 |  | 1 | 22 | 20 | FC22/1 | Enter Custom Fixture |  |  | Enter Custom Fixture
FC22/32/1 | Circular Fluorescent | Circular Fluorescent | FC22/32T9 | Fluorescent, Circlite, (1) 22W/32W lamp, preheat ballast | Mag-STD | 1 |  | 1 | 22/32 | 58 | FC22/32/1 | Enter Custom Fixture |  |  | Enter Custom Fixture
FC32/1 | Circular Fluorescent | Circular Fluorescent | FC12T9 | Fluorescent, Circline, (1) 32W lamp, preheat ballast | Mag-STD | 1 |  | 1 | 32 | 40 | FC32/1 | Enter Custom Fixture |  |  | Enter Custom Fixture
FC32/40/1 | Circular Fluorescent | Circular Fluorescent | FC32/40T9 | Fluorescent, Circlite, (1) 32W/40W lamp, preheat ballast | Mag-STD | 1 |  | 1 | 32/40 | 80 | FC32/40/1 | Enter Custom Fixture |  |  | Enter Custom Fixture
FC40/1 | Circular Fluorescent | Circular Fluorescent | FC16T9 | Fluorescent, Circline, (1) 32W lamp, preheat ballast | Mag-STD | 1 |  | 1 | 32 | 42 | FC40/1 | Enter Custom Fixture |  |  | Enter Custom Fixture
FC44/1 | Circular Fluorescent | Circular Fluorescent | FC44T9 | Fluorescent, Circlite, (1) 44W lamp, preheat ballast | Mag-STD | 1 |  | 1 | 44 | 46 | FC44/1 | Enter Custom Fixture |  |  | Enter Custom Fixture
FC6/1 | Circular Fluorescent | Circular Fluorescent | FC6T9 | Fluorescent, (1) 6" circular lamp, RS ballast | Mag-STD | 1 | 6 | 1 | 20 | 25 | FC6/1 | Enter Custom Fixture |  |  | Enter Custom Fixture
FC8/1 | Circular Fluorescent | Circular Fluorescent | FC8T9 | Fluorescent, (1) 8" circular lamp, RS ballast | Mag-STD | 1 | 8 | 1 | 22 | 26 | FC8/1 | Enter Custom Fixture |  |  | Enter Custom Fixture
FC8/2 | Circular Fluorescent | Circular Fluorescent | FC8T9 | Fluorescent, (2) 8" circular lamp, RS ballast | Mag-STD | 1 | 8 | 2 | 22 | 52 | FC8/2 | Enter Custom Fixture |  |  | Enter Custom Fixture
F40EE/D1 | Delamp | Delamp | None | Fluorescent, (0) 48" lamp, Completely delamped fixture with (1) hot ballast | Mag-ES | 1 |  | 0 | 0 | 4 | F40EE/D1 | Enter Custom Fixture |  |  | Enter Custom Fixture
F40EE/D2 | Delamp | Delamp | None | Fluorescent, (0) 48" lamp, Completely delamped fixture with (2) hot ballast | Mag-ES | 1 |  | 0 | 0 | 8 | F40EE/D2 | Enter Custom Fixture |  |  | Enter Custom Fixture
ECF5/1 | Exit Sign | Exit Sign | CFT5W | EXIT Compact Fluorescent, (1) 5W lamp | Mag-STD | 1 |  | 1 | 5 | 9 | ECF5/1 | Enter Custom Fixture |  |  | Enter Custom Fixture
ECF5/2 | Exit Sign | Exit Sign | CFT5W | EXIT Compact Fluorescent, (2) 5W lamp | Mag-STD | 1 |  | 2 | 5 | 20 | ECF5/2 | Enter Custom Fixture |  |  | Enter Custom Fixture
ECF7/1 | Exit Sign | Exit Sign | CFT7W | EXIT Compact Fluorescent, (1) 7W lamp | Mag-STD | 1 |  | 1 | 7 | 10 | ECF7/1 | Enter Custom Fixture |  |  | Enter Custom Fixture
ECF7/2 | Exit Sign | Exit Sign | CFT7W | EXIT Compact Fluorescent, (2) 7W lamp | Mag-STD | 1 |  | 2 | 7 | 21 | ECF7/2 | Enter Custom Fixture |  |  | Enter Custom Fixture
ECF8/1 | Exit Sign | Exit Sign | F8T5 | EXIT T5 Fluorescent, (1) 8W lamp | Mag-STD | 1 |  | 1 | 8 | 12 | ECF8/1 | Enter Custom Fixture |  |  | Enter Custom Fixture
ECF8/2 | Exit Sign | Exit Sign | F8T5 | EXIT T5 Fluorescent, (2) 8W lamp | Mag-STD | 1 |  | 2 | 8 | 24 | ECF8/2 | Enter Custom Fixture |  |  | Enter Custom Fixture
ECF9/1 | Exit Sign | Exit Sign | CFT9W | EXIT Compact Fluorescent, (1) 9W lamp | Mag-STD | 1 |  | 1 | 9 | 12 | ECF9/1 | Enter Custom Fixture |  |  | Enter Custom Fixture
ECF9/2 | Exit Sign | Exit Sign | CFT9W | EXIT Compact Fluorescent, (2) 9W lamp | Mag-STD | 1 |  | 2 | 9 | 20 | ECF9/2 | Enter Custom Fixture |  |  | Enter Custom Fixture
EI10/2 | Exit Sign | Exit Sign | I10 | EXIT Incandescent, (2) 10W lamp |  |  |  | 2 | 10 | 20 | EI10/2 | Enter Custom Fixture
EI15/1 | Exit Sign | Exit Sign | I15 | EXIT Incandescent, (1) 15W lamp |  |  |  | 1 | 15 | 15 | EI15/1 | Enter Custom Fixture
EI15/2 | Exit Sign | Exit Sign | I15 | EXIT Incandescent, (2) 15W lamp |  |  |  | 2 | 15 | 30 | EI15/2 | Enter Custom Fixture
EI20/1 | Exit Sign | Exit Sign | I20 | EXIT Incandescent, (1) 20W lamp |  |  |  | 1 | 20 | 20 | EI20/1 | Enter Custom Fixture
EI20/2 | Exit Sign | Exit Sign | I20 | EXIT Incandescent, (2) 20W lamp |  |  |  | 2 | 20 | 40 | EI20/2 | Enter Custom Fixture
EI25/1 | Exit Sign | Exit Sign | I25 | EXIT Incandescent, (1) 25W lamp |  |  |  | 1 | 25 | 25 | EI25/1 | Enter Custom Fixture
EI25/2 | Exit Sign | Exit Sign | I25 | EXIT Incandescent, (2) 25W lamp |  |  |  | 2 | 25 | 50 | EI25/2 | Enter Custom Fixture
EI34/1 | Exit Sign | Exit Sign | I34 | EXIT Incandescent, (1) 34W lamp |  |  |  | 1 | 34 | 34 | EI34/1 | Enter Custom Fixture
EI34/2 | Exit Sign | Exit Sign | I34 | EXIT Incandescent, (2) 34W lamp |  |  |  | 2 | 34 | 68 | EI34/2 | Enter Custom Fixture
EI40/1 | Exit Sign | Exit Sign | I40 | EXIT Incandescent, (1) 40W lamp |  |  |  | 1 | 40 | 40 | EI40/1 | Enter Custom Fixture
EI40/2 | Exit Sign | Exit Sign | I40 | EXIT Incandescent, (2) 40W lamp |  |  |  | 2 | 40 | 80 | EI40/2 | Enter Custom Fixture
EI5/1 | Exit Sign | Exit Sign | I5 | EXIT Incandescent, (1) 5W lamp |  |  |  | 1 | 5 | 5 | EI5/1 | Enter Custom Fixture
EI5/2 | Exit Sign | Exit Sign | I5 | EXIT Incandescent, (2) 5W lamp |  |  |  | 2 | 5 | 10 | EI5/2 | Enter Custom Fixture
EI50/2 | Exit Sign | Exit Sign | I50 | EXIT Incandescent, (2) 50W lamp |  |  |  | 2 | 50 | 100 | EI50/2 | Enter Custom Fixture
EI7.5/1 | Exit Sign | Exit Sign | I7.5 | EXIT Tungsten, (1) 7.5 W lamp |  |  |  | 1 | 7.5 | 8 | EI7.5/1 | Enter Custom Fixture
EI7.5/2 | Exit Sign | Exit Sign | I7.5 | EXIT Tungsten, (2) 7.5 W lamp |  |  |  | 2 | 7.5 | 15 | EI7.5/2 | Enter Custom Fixture
ELED0.5/1 | Exit Sign | Exit Sign | LED0.5W | EXIT Light Emitting Diode, (1) 0.5W lamp, Single Sided |  |  |  | 1 | 0.5 | 0.5 | ELED0.5/1 | Enter Custom Fixture
ELED0.5/2 | Exit Sign | Exit Sign | LED0.5W | EXIT Light Emitting Diode, (2) 0.5W lamp, Dual Sided |  |  |  | 2 | 0.5 | 1 | ELED0.5/2 | Enter Custom Fixture
ELED1.5/1 | Exit Sign | Exit Sign | LED1.5W | EXIT Light Emitting Diode, (1) 1.5W lamp, Single Sided |  |  |  | 1 | 1.5 | 1.5 | ELED1.5/1 | Enter Custom Fixture
ELED1.5/2 | Exit Sign | Exit Sign | LED1.5W | EXIT Light Emitting Diode, (2) 1.5W lamp, Dual Sided |  |  |  | 2 | 1.5 | 3 | ELED1.5/2 | Enter Custom Fixture
ELED10.5/1 | Exit Sign | Exit Sign | LED10.5W | EXIT Light Emitting Diode, (1) 10.5W lamp, Single Sided |  |  |  | 1 | 10.5 | 10.5 | ELED10.5/1 | Enter Custom Fixture
ELED10.5/2 | Exit Sign | Exit Sign | LED10.5W | EXIT Light Emitting Diode, (2) 10.5W lamp, Dual Sided |  |  |  | 2 | 10.5 | 21 | ELED10.5/2 | Enter Custom Fixture
ELED2/1 | Exit Sign | Exit Sign | LED2W | EXIT Light Emitting Diode, (1) 2W lamp, Single Sided |  |  |  | 1 | 2 | 2 | ELED2/1 | Enter Custom Fixture
ELED2/2 | Exit Sign | Exit Sign | LED2W | EXIT Light Emitting Diode, (2) 2W lamp, Dual Sided |  |  |  | 2 | 2 | 4 | ELED2/2 | Enter Custom Fixture
ELED3/1 | Exit Sign | Exit Sign | LED3W | EXIT Light Emitting Diode, (1) 3W lamp, Single Sided |  |  |  | 1 | 3 | 3 | ELED3/1 | Enter Custom Fixture
ELED3/2 | Exit Sign | Exit Sign | LED3W | EXIT Light Emitting Diode, (2) 3W lamp, Dual Sided |  |  |  | 2 | 3 | 6 | ELED3/2 | Enter Custom Fixture
ELED5/1 | Exit Sign | Exit Sign | LED5W | EXIT Light Emitting Diode, (1) 5W lamp, Single Sided |  |  |  | 1 | 5 | 5 | ELED5/1 | Enter Custom Fixture
ELED5/2 | Exit Sign | Exit Sign | LED5W | EXIT Light Emitting Diode, (2) 5W lamp, Dual Sided |  |  |  | 2 | 5 | 10 | ELED5/2 | Enter Custom Fixture
ELED8/1 | Exit Sign | Exit Sign | LED8W | EXIT Light Emitting Diode, (1) 8W lamp, Single Sided |  |  |  | 1 | 8 | 8 | ELED8/1 | Enter Custom Fixture
ELED8/2 | Exit Sign | Exit Sign | LED8W | EXIT Light Emitting Diode, (2) 8W lamp, Dual Sided |  |  |  | 2 | 8 | 16 | ELED8/2 | Enter Custom Fixture
HPS100/1 | High Intensity Discharge | High Pressure Sodium | HPS100 | High Pressure Sodium, (1) 100W lamp | CWA | 1 |  | 1 | 100 | 138 | HPS100/1 | Enter Custom Fixture
HPS1000/1 | High Intensity Discharge | High Pressure Sodium | HPS1000 | High Pressure Sodium, (1) 1000W lamp | CWA | 1 |  | 1 | 1000 | 1100 | HPS1000/1 | Enter Custom Fixture
HPS150/1 | High Intensity Discharge | High Pressure Sodium | HPS150 | High Pressure Sodium, (1) 150W lamp | CWA | 1 |  | 1 | 150 | 188 | HPS150/1 | Enter Custom Fixture
HPS200/1 | High Intensity Discharge | High Pressure Sodium | HPS200 | High Pressure Sodium, (1) 200W lamp | CWA | 1 |  | 1 | 200 | 250 | HPS200/1 | Enter Custom Fixture
HPS225/1 | High Intensity Discharge | High Pressure Sodium | HPS225 | High Pressure Sodium, (1) 225W lamp | CWA | 1 |  | 1 | 225 | 275 | HPS225/1 | Enter Custom Fixture
HPS250/1 | High Intensity Discharge | High Pressure Sodium | HPS250 | High Pressure Sodium, (1) 250W lamp | CWA | 1 |  | 1 | 250 | 295 | HPS250/1
HPS310/1 | High Intensity Discharge | High Pressure Sodium | HPS310 | High Pressure Sodium, (1) 310W lamp | CWA | 1 |  | 1 | 310 | 365 | HPS310/1
HPS35/1 | High Intensity Discharge | High Pressure Sodium | HPS35 | High Pressure Sodium, (1) 35W lamp | CWA | 1 |  | 1 | 35 | 46 | HPS35/1
HPS360/1 | High Intensity Discharge | High Pressure Sodium | HPS360 | High Pressure Sodium, (1) 360W lamp | CWA | 1 |  | 1 | 360 | 414 | HPS360/1
HPS400/1 | High Intensity Discharge | High Pressure Sodium | HPS400 | High Pressure Sodium, (1) 400W lamp | CWA | 1 |  | 1 | 400 | 465 | HPS400/1
HPS50/1 | High Intensity Discharge | High Pressure Sodium | HPS50 | High Pressure Sodium, (1) 50W lamp | CWA | 1 |  | 1 | 50 | 66 | HPS50/1
HPS600/1 | High Intensity Discharge | High Pressure Sodium | HPS600 | High Pressure Sodium, (1) 600W lamp | CWA | 1 |  | 1 | 600 | 675 | HPS600/1
HPS70/1 | High Intensity Discharge | High Pressure Sodium | HPS70 | High Pressure Sodium, (1) 70W lamp | CWA | 1 |  | 1 | 70 | 95 | HPS70/1
HPS750/1 | High Intensity Discharge | High Pressure Sodium | HPS750 | High Pressure Sodium, (1) 750W lamp | CWA | 1 |  | 1 | 750 | 835 | HPS750/1
MH100/1 | High Intensity Discharge | Metal Halide | MH100 | Metal Halide, (1) 100W lamp | CWA | 1 |  | 1 | 100 | 128 | MH100/1
MH1000/1 | High Intensity Discharge | Metal Halide | MH1000 | Metal Halide, (1) 1000W lamp | CWA | 1 |  | 1 | 1000 | 1080 | MH1000/1
MH150/1 | High Intensity Discharge | Metal Halide | MH150 | Metal Halide, (1) 150W lamp | CWA | 1 |  | 1 | 150 | 190 | MH150/1
MH1500/1 | High Intensity Discharge | Metal Halide | MH1500 | Metal Halide, (1) 1500W lamp | CWA | 1 |  | 1 | 1500 | 1610 | MH1500/1
MH175/1 | High Intensity Discharge | Metal Halide | MH175 | Metal Halide, (1) 175W lamp | CWA | 1 |  | 1 | 175 | 215 | MH175/1
MH1800/1 | High Intensity Discharge | Metal Halide | MH1800 | Metal Halide, (1) 1800W lamp | CWA | 1 |  | 1 | 1800 | 1875 | MH1800/1
MH200/1 | High Intensity Discharge | Metal Halide | MH200 | Metal Halide, (1) 200W lamp | CWA | 1 |  | 1 | 200 | 232 | MH200/1
MH250/1 | High Intensity Discharge | Metal Halide | MH250 | Metal Halide, (1) 250W lamp | CWA | 1 |  | 1 | 250 | 295 | MH250/1
MH300/1 | High Intensity Discharge | Metal Halide | MH300 | Metal Halide, (1) 300W lamp | CWA | 1 |  | 1 | 300 | 342 | MH300/1
MH32/1 | High Intensity Discharge | Metal Halide | MH32 | Metal Halide, (1) 32W lamp | CWA | 1 |  | 1 | 32 | 43 | MH32/1
MH320/1 | High Intensity Discharge | Metal Halide | MH320 | Metal Halide, (1) 320W lamp | CWA | 1 |  | 1 | 320 | 365 | MH320/1
MH35/1 | High Intensity Discharge | Metal Halide | MH35 | Metal Halide, (1) 35W lamp | CWA | 1 |  | 1 | 35 | 44 | MH35/1
MH350/1 | High Intensity Discharge | Metal Halide | MH350 | Metal Halide, (1) 350W lamp | CWA | 1 |  | 1 | 350 | 400 | MH350/1
MH360/1 | High Intensity Discharge | Metal Halide | MH360 | Metal Halide, (1) 360W lamp | CWA | 1 |  | 1 | 360 | 430 | MH360/1
MH400/1 | High Intensity Discharge | Metal Halide | MH400 | Metal Halide, (1) 400W lamp | CWA | 1 |  | 1 | 400 | 458 | MH400/1
MH400/2 | High Intensity Discharge | Metal Halide | MH400 | Metal Halide, (2) 400W lamp | CWA | 1 |  | 2 | 400 | 916 | MH400/2
MH450/1 | High Intensity Discharge | Metal Halide | MH450 | Metal Halide, (1) 450W lamp | CWA | 1 |  | 1 | 450 | 508 | MH450/1
MH50/1 | High Intensity Discharge | Metal Halide | MH50 | Metal Halide, (1) 50W lamp | CWA | 1 |  | 1 | 50 | 72 | MH50/1
MH70/1 | High Intensity Discharge | Metal Halide | MH70 | Metal Halide, (1) 70W lamp | CWA | 1 |  | 1 | 70 | 95 | MH70/1
MH750/1 | High Intensity Discharge | Metal Halide | MH750 | Metal Halide, (1) 750W lamp | CWA | 1 |  | 1 | 750 | 850 | MH750/1
MHPS/LR/100/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS100 | Metal Halide Pulse Start, (1) 100W lamp w/ Linear Reactor Ballast | LR | 1 |  | 1 | 100 | 118 | MHPS/LR/100/1
MHPS/LR/150/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS150 | Metal Halide Pulse Start, (1) 150W lamp w/ Linear Reactor Ballast | LR | 1 |  | 1 | 150 | 170 | MHPS/LR/150/1
MHPS/LR/175/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS175 | Metal Halide Pulse Start, (1) 175W lamp w/ Linear Reactor Ballast | LR | 1 |  | 1 | 175 | 194 | MHPS/LR/175/1
MHPS/LR/200/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS200 | Metal Halide Pulse Start, (1) 200W lamp w/ Linear Reactor Ballast | LR | 1 |  | 1 | 200 | 219 | MHPS/LR/200/1
MHPS/LR/250/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS250 | Metal Halide Pulse Start, (1) 250W lamp w/ Linear Reactor Ballast | LR | 1 |  | 1 | 250 | 275 | MHPS/LR/250/1
MHPS/LR/300/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS300 | Metal Halide Pulse Start, (1) 300W lamp w/ Linear Reactor Ballast | LR | 1 |  | 1 | 300 | 324 | MHPS/LR/300/1
MHPS/LR/320/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS320 | Metal Halide Pulse Start, (1) 320W lamp w/ Linear Reactor Ballast | LR | 1 |  | 1 | 320 | 349 | MHPS/LR/320/1
MHPS/LR/350/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS350 | Metal Halide Pulse Start, (1) 350W lamp w/ Linear Reactor Ballast | LR | 1 |  | 1 | 350 | 380 | MHPS/LR/350/1
MHPS/LR/400/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS400 | Metal Halide Pulse Start, (1) 400W lamp w/ Linear Reactor Ballast | LR | 1 |  | 1 | 400 | 435 | MHPS/LR/400/1
MHPS/LR/450/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS450 | Metal Halide Pulse Start, (1) 450W lamp w/ Linear Reactor Ballast | LR | 1 |  | 1 | 450 | 485 | MHPS/LR/450/1
MHPS/LR/750/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS750 | Metal Halide Pulse Start, (1) 750W lamp w/ Linear Reactor Ballast | LR | 1 |  | 1 | 750 | 805 | MHPS/LR/750/1
MHPS/SCWA/100/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS100 | Metal Halide Pulse Start, (1) 100W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA | 1 |  | 1 | 100 | 128 | MHPS/SCWA/100/1
MHPS/SCWA/1000/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS1000 | Metal Halide Pulse Start, (1) 1000W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA | 1 |  | 1 | 1000 | 1080 | MHPS/SCWA/1000/1
MHPS/SCWA/150/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS150 | Metal Halide Pulse Start, (1) 150W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA | 1 |  | 1 | 150 | 190 | MHPS/SCWA/150/1
MHPS/SCWA/175/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS175 | Metal Halide Pulse Start, (1) 175W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA | 1 |  | 1 | 175 | 208 | MHPS/SCWA/175/1
MHPS/SCWA/200/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS200 | Metal Halide Pulse Start, (1) 200W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA | 1 |  | 1 | 200 | 232 | MHPS/SCWA/200/1
MHPS/SCWA/250/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS250 | Metal Halide Pulse Start, (1) 250W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA | 1 |  | 1 | 250 | 288 | MHPS/SCWA/250/1
MHPS/SCWA/300/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS300 | Metal Halide Pulse Start, (1) 300W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA | 1 |  | 1 | 300 | 342 | MHPS/SCWA/300/1
MHPS/SCWA/320/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS320 | Metal Halide Pulse Start, (1) 320W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA | 1 |  | 1 | 320 | 368 | MHPS/SCWA/320/1
MHPS/SCWA/350/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS350 | Metal Halide Pulse Start, (1) 350W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA | 1 |  | 1 | 350 | 400 | MHPS/SCWA/350/1
MHPS/SCWA/400/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS400 | Metal Halide Pulse Start, (1) 400W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA | 1 |  | 1 | 400 | 450 | MHPS/SCWA/400/1
MHPS/SCWA/450/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS450 | Metal Halide Pulse Start, (1) 450W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA | 1 |  | 1 | 450 | 506 | MHPS/SCWA/450/1
MHPS/SCWA/750/1 | High Intensity Discharge | Pulse Start Metal Halide | MHPS750 | Metal Halide Pulse Start, (1) 750W lamp w/ Super Constant Wattage Autotransformer Ballast | SCWA | 1 |  | 1 | 750 | 815 | MHPS/SCWA/750/1
MV100/1 | High Intensity Discharge | Mercury Vapor | MV100 | Mercury Vapor, (1) 100W lamp | CWA | 1 |  | 1 | 100 | 125 | MV100/1
MV1000/1 | High Intensity Discharge | Mercury Vapor | MV1000 | Mercury Vapor, (1) 1000W lamp | CWA | 1 |  | 1 | 1000 | 1075 | MV1000/1
MV175/1 | High Intensity Discharge | Mercury Vapor | MV175 | Mercury Vapor, (1) 175W lamp | CWA | 1 |  | 1 | 175 | 205 | MV175/1
MV250/1 | High Intensity Discharge | Mercury Vapor | MV250 | Mercury Vapor, (1) 250W lamp | CWA | 1 |  | 1 | 250 | 290 | MV250/1
MV40/1 | High Intensity Discharge | Mercury Vapor | MV40 | Mercury Vapor, (1) 40W lamp | CWA | 1 |  | 1 | 40 | 50 | MV40/1
MV400/1 | High Intensity Discharge | Mercury Vapor | MV400 | Mercury Vapor, (1) 400W lamp | CWA | 1 |  | 1 | 400 | 455 | MV400/1
MV400/2 | High Intensity Discharge | Mercury Vapor | MV400 | Mercury Vapor, (2) 400W lamp | CWA | 1 |  | 2 | 400 | 910 | MV400/2
MV50/1 | High Intensity Discharge | Mercury Vapor | MV50 | Mercury Vapor, (1) 50W lamp | CWA | 1 |  | 1 | 50 | 74 | MV50/1
MV700/1 | High Intensity Discharge | Mercury Vapor | MV700 | Mercury Vapor, (1) 700W lamp | CWA | 1 |  | 1 | 700 | 780 | MV700/1
MV75/1 | High Intensity Discharge | Mercury Vapor | MV75 | Mercury Vapor, (1) 75W lamp | CWA | 1 |  | 1 | 75 | 93 | MV75/1
H100/1 | Incandescent | Halogen Incandescent | H100 | Halogen Incandescent, (1) 100W lamp |  |  |  | 1 | 100 | 100 | H100/1
H1000/1 | Incandescent | Halogen Incandescent | H1000 | Halogen Incandescent, (1) 1000W lamp |  |  |  | 1 | 1000 | 1000 | H1000/1
H1200/1 | Incandescent | Halogen Incandescent | H1200 | Halogen Incandescent, (1) 1200W lamp |  |  |  | 1 | 1200 | 1200 | H1200/1
H150/1 | Incandescent | Halogen Incandescent | H150 | Halogen Incandescent, (1) 150W lamp |  |  |  | 1 | 150 | 150 | H150/1
H150/2 | Incandescent | Halogen Incandescent | H150 | Halogen Incandescent, (2) 150W lamp |  |  |  | 2 | 150 | 300 | H150/2
H1500/1 | Incandescent | Halogen Incandescent | H1500 | Halogen Incandescent, (1) 1500W lamp |  |  |  | 1 | 1500 | 1500 | H1500/1
H200/1 | Incandescent | Halogen Incandescent | H200 | Halogen Incandescent, (1) 200W lamp |  |  |  | 1 | 200 | 200 | H200/1
H250/1 | Incandescent | Halogen Incandescent | H250 | Halogen Incandescent, (1) 250W lamp |  |  |  | 1 | 250 | 250 | H250/1
H300/1 | Incandescent | Halogen Incandescent | H300 | Halogen Incandescent, (1) 300W lamp |  |  |  | 1 | 300 | 300 | H300/1
H35/1 | Incandescent | Halogen Incandescent | H35 | Halogen Incandescent, (1) 35W lamp |  |  |  | 1 | 35 | 35 | H35/1
H350/1 | Incandescent | Halogen Incandescent | H350 | Halogen Incandescent, (1) 350W lamp |  |  |  | 1 | 350 | 350 | H350/1
H40/1 | Incandescent | Halogen Incandescent | H40 | Halogen Incandescent, (1) 40W lamp |  |  |  | 1 | 40 | 40 | H40/1
H400/1 | Incandescent | Halogen Incandescent | H400 | Halogen Incandescent, (1) 400W lamp |  |  |  | 1 | 400 | 400 | H400/1
H42/1 | Incandescent | Halogen Incandescent | H42 | Halogen Incandescent, (1) 42W lamp |  |  |  | 1 | 42 | 42 | H42/1
H425/1 | Incandescent | Halogen Incandescent | H425 | Halogen Incandescent, (1) 425W lamp |  |  |  | 1 | 425 | 425 | H425/1
H45/1 | Incandescent | Halogen Incandescent | H45 | Halogen Incandescent, (1) 45W lamp |  |  |  | 1 | 45 | 45 | H45/1
H45/2 | Incandescent | Halogen Incandescent | H45 | Halogen Incandescent, (2) 45W lamp |  |  |  | 2 | 45 | 90 | H45/2
H50/1 | Incandescent | Halogen Incandescent | H50 | Halogen Incandescent, (1) 50W lamp |  |  |  | 1 | 50 | 50 | H50/1
H50/2 | Incandescent | Halogen Incandescent | H50 | Halogen Incandescent, (2) 50W lamp |  |  |  | 2 | 50 | 100 | H50/2
H500/1 | Incandescent | Halogen Incandescent | H500 | Halogen Incandescent, (1) 500W lamp |  |  |  | 1 | 500 | 500 | H500/1
H52/1 | Incandescent | Halogen Incandescent | H52 | Halogen Incandescent, (1) 52W lamp |  |  |  | 1 | 52 | 52 | H52/1
H55/1 | Incandescent | Halogen Incandescent | H55 | Halogen Incandescent, (1) 55W lamp |  |  |  | 1 | 55 | 55 | H55/1
H55/2 | Incandescent | Halogen Incandescent | H55 | Halogen Incandescent, (2) 55W lamp |  |  |  | 2 | 55 | 110 | H55/2
H60/1 | Incandescent | Halogen Incandescent | H60 | Halogen Incandescent, (1) 60W lamp |  |  |  | 1 | 60 | 60 | H60/1
H72/1 | Incandescent | Halogen Incandescent | H72 | Halogen Incandescent, (1) 72W lamp |  |  |  | 1 | 72 | 72 | H72/1
H75/1 | Incandescent | Halogen Incandescent | H75 | Halogen Incandescent, (1) 75W lamp |  |  |  | 1 | 75 | 75 | H75/1
H75/2 | Incandescent | Halogen Incandescent | H75 | Halogen Incandescent, (2) 75W lamp |  |  |  | 2 | 75 | 150 | H75/2
H750/1 | Incandescent | Halogen Incandescent | H750 | Halogen Incandescent, (1) 750W lamp |  |  |  | 1 | 750 | 750 | H750/1
H90/1 | Incandescent | Halogen Incandescent | H90 | Halogen Incandescent, (1) 90W lamp |  |  |  | 1 | 90 | 90 | H90/1
H90/2 | Incandescent | Halogen Incandescent | H90 | Halogen Incandescent, (2) 90W lamp |  |  |  | 2 | 90 | 180 | H90/2
H900/1 | Incandescent | Halogen Incandescent | H900 | Halogen Incandescent, (1) 900W lamp |  |  |  | 1 | 900 | 900 | H900/1
HLV20/1 | Incandescent | Halogen Incandescent | H20/LV | Halogen Low Voltage Incandescent, (1) 20W lamp |  |  |  | 1 | 20 | 30 | HLV20/1
HLV25/1 | Incandescent | Halogen Incandescent | H25/LV | Halogen Low Voltage Incandescent, (1) 25W lamp |  |  |  | 1 | 25 | 35 | HLV25/1
HLV35/1 | Incandescent | Halogen Incandescent | H35/LV | Halogen Low Voltage Incandescent, (1) 35W lamp |  |  |  | 1 | 35 | 45 | HLV35/1
HLV42/1 | Incandescent | Halogen Incandescent | H42/LV | Halogen Low Voltage Incandescent, (1) 42W lamp |  |  |  | 1 | 42 | 52 | HLV42/1
HLV50/1 | Incandescent | Halogen Incandescent | H50/LV | Halogen Low Voltage Incandescent, (1) 50W lamp |  |  |  | 1 | 50 | 60 | HLV50/1
HLV65/1 | Incandescent | Halogen Incandescent | H65/LV | Halogen Low Voltage Incandescent, (1) 65W lamp |  |  |  | 1 | 65 | 75 | HLV65/1
HLV75/1 | Incandescent | Halogen Incandescent | H75/LV | Halogen Low Voltage Incandescent, (1) 75W lamp |  |  |  | 1 | 75 | 85 | HLV75/1
I100/1 | Incandescent | Standard Incandescent | I100 | Incandescent, (1) 100W lamp |  |  |  | 1 | 100 | 100 | I100/1
I100/2 | Incandescent | Standard Incandescent | I100 | Incandescent, (2) 100W lamp |  |  |  | 2 | 100 | 200 | I100/2
I100/3 | Incandescent | Standard Incandescent | I100 | Incandescent, (3) 100W lamp |  |  |  | 3 | 100 | 300 | I100/3
I100/4 | Incandescent | Standard Incandescent | I100 | Incandescent, (4) 100W lamp |  |  |  | 4 | 100 | 400 | I100/4
I100/5 | Incandescent | Standard Incandescent | I100 | Incandescent, (5) 100W lamp |  |  |  | 5 | 100 | 500 | I100/5
I1000/1 | Incandescent | Standard Incandescent | I1000 | Incandescent, (1) 1000W lamp |  |  |  | 1 | 1000 | 1000 | I1000/1
I100E/1 | Incandescent | Standard Incandescent | I100/ES | Incandescent, (1) 100W ES lamp |  |  |  | 1 | 90 | 90 | I100E/1
I100EL/1 | Incandescent | Standard Incandescent | I100/ES/LL | Incandescent, (1) 100W ES/LL lamp |  |  |  | 1 | 90 | 90 | I100EL/1
I120/1 | Incandescent | Standard Incandescent | I120 | Incandescent, (1) 120W lamp |  |  |  | 1 | 120 | 120 | I120/1
I120/2 | Incandescent | Standard Incandescent | I120 | Incandescent, (2) 120W lamp |  |  |  | 2 | 120 | 240 | I120/2
I125/1 | Incandescent | Standard Incandescent | I125 | Incandescent, (1) 125W lamp |  |  |  | 1 | 125 | 125 | I125/1
I135/1 | Incandescent | Standard Incandescent | I135 | Incandescent, (1) 135W lamp |  |  |  | 1 | 135 | 135 | I135/1
I135/2 | Incandescent | Standard Incandescent | I135 | Incandescent, (2) 135W lamp |  |  |  | 2 | 135 | 270 | I135/2
I15/1 | Incandescent | Standard Incandescent | I15 | Incandescent, (1) 15W lamp |  |  |  | 1 | 15 | 15 | I15/1
I15/2 | Incandescent | Standard Incandescent | I15 | Incandescent, (2) 15W lamp |  |  |  | 2 | 15 | 30 | I15/2
I150/1 | Incandescent | Standard Incandescent | I150 | Incandescent, (1) 150W lamp |  |  |  | 1 | 150 | 150 | I150/1
I150/2 | Incandescent | Standard Incandescent | I150 | Incandescent, (2) 150W lamp |  |  |  | 2 | 150 | 300 | I150/2
I1500/1 | Incandescent | Standard Incandescent | I1500 | Incandescent, (1) 1500W lamp |  |  |  | 1 | 1500 | 1500 | I1500/1
I150E/1 | Incandescent | Standard Incandescent | I150/ES | Incandescent, (1) 150W ES lamp |  |  |  | 1 | 135 | 135 | I150E/1
I150EL/1 | Incandescent | Standard Incandescent | I150/ES/LL | Incandescent, (1) 150W ES/LL lamp |  |  |  | 1 | 135 | 135 | I150EL/1
I170/1 | Incandescent | Standard Incandescent | I170 | Incandescent, (1) 170W lamp |  |  |  | 1 | 170 | 170 | I170/1
I20/1 | Incandescent | Standard Incandescent | I20 | Incandescent, (1) 20W lamp |  |  |  | 1 | 20 | 20 | I20/1
I20/2 | Incandescent | Standard Incandescent | I20 | Incandescent, (2) 20W lamp |  |  |  | 2 | 20 | 40 | I20/2
I200/1 | Incandescent | Standard Incandescent | I200 | Incandescent, (1) 200W lamp |  |  |  | 1 | 200 | 200 | I200/1
I200/2 | Incandescent | Standard Incandescent | I200 | Incandescent, (2) 200W lamp |  |  |  | 2 | 200 | 400 | I200/2
I2000/1 | Incandescent | Standard Incandescent | I2000 | Incandescent, (1) 2000W lamp |  |  |  | 1 | 2000 | 2000 | I2000/1
I200L/1 | Incandescent | Standard Incandescent | I200/LL | Incandescent, (1) 200W LL lamp |  |  |  | 1 | 200 | 200 | I200L/1
I25/1 | Incandescent | Standard Incandescent | I25 | Incandescent, (1) 25W lamp |  |  |  | 1 | 25 | 25 | I25/1
I25/2 | Incandescent | Standard Incandescent | I25 | Incandescent, (2) 25W lamp |  |  |  | 2 | 25 | 50 | I25/2
I25/4 | Incandescent | Standard Incandescent | I25 | Incandescent, (4) 25W lamp |  |  |  | 4 | 25 | 100 | I25/4
I250/1 | Incandescent | Standard Incandescent | I250 | Incandescent, (1) 250W lamp |  |  |  | 1 | 250 | 250 | I250/1
I300/1 | Incandescent | Standard Incandescent | I300 | Incandescent, (1) 300W lamp |  |  |  | 1 | 300 | 300 | I300/1
I34/1 | Incandescent | Standard Incandescent | I34 | Incandescent, (1) 34W lamp |  |  |  | 1 | 34 | 34 | I34/1
I34/2 | Incandescent | Standard Incandescent | I34 | Incandescent, (2) 34W lamp |  |  |  | 2 | 34 | 68 | I34/2
I36/1 | Incandescent | Standard Incandescent | I36 | Incandescent, (1) 36W lamp |  |  |  | 1 | 36 | 36 | I36/1
I40/1 | Incandescent | Standard Incandescent | I40 | Incandescent, (1) 40W lamp |  |  |  | 1 | 40 | 40 | I40/1
I40/2 | Incandescent | Standard Incandescent | I40 | Incandescent, (2) 40W lamp |  |  |  | 2 | 40 | 80 | I40/2
I400/1 | Incandescent | Standard Incandescent | I400 | Incandescent, (1) 400W lamp |  |  |  | 1 | 400 | 400 | I400/1
I40E/1 | Incandescent | Standard Incandescent | I40/ES | Incandescent, (1) 40W ES lamp |  |  |  | 1 | 34 | 34 | I40E/1
I40EL/1 | Incandescent | Standard Incandescent | I40/ES/LL | Incandescent, (1) 40W ES/LL lamp |  |  |  | 1 | 34 | 34 | I40EL/1
I42/1 | Incandescent | Standard Incandescent | I42 | Incandescent, (1) 42W lamp |  |  |  | 1 | 42 | 42 | I42/1
I448/1 | Incandescent | Standard Incandescent | I448 | Incandescent, (1) 448W lamp |  |  |  | 1 | 448 | 448 | I448/1
I45/1 | Incandescent | Standard Incandescent | I45 | Incandescent, (1) 45W lamp |  |  |  | 1 | 45 | 45 | I45/1
I50/1 | Incandescent | Standard Incandescent | I50 | Incandescent, (1) 50W lamp |  |  |  | 1 | 50 | 50 | I50/1
I50/2 | Incandescent | Standard Incandescent | I50 | Incandescent, (2) 50W lamp |  |  |  | 2 | 50 | 100 | I50/2
I500/1 | Incandescent | Standard Incandescent | I500 | Incandescent, (1) 500W lamp |  |  |  | 1 | 500 | 500 | I500/1
I52/1 | Incandescent | Standard Incandescent | I52 | Incandescent, (1) 52W lamp |  |  |  | 1 | 52 | 52 | I52/1
I52/2 | Incandescent | Standard Incandescent | I52 | Incandescent, (2) 52W lamp |  |  |  | 2 | 52 | 104 | I52/2
I54/1 | Incandescent | Standard Incandescent | I54 | Incandescent, (1) 54W lamp |  |  |  | 1 | 54 | 54 | I54/1
I54/2 | Incandescent | Standard Incandescent | I54 | Incandescent, (2) 54W lamp |  |  |  | 2 | 54 | 108 | I54/2
I55/1 | Incandescent | Standard Incandescent | I55 | Incandescent, (1) 55W lamp |  |  |  | 1 | 55 | 55 | I55/1
I55/2 | Incandescent | Standard Incandescent | I55 | Incandescent, (2) 55W lamp |  |  |  | 2 | 55 | 110 | I55/2
I60/1 | Incandescent | Standard Incandescent | I60 | Incandescent, (1) 60W lamp |  |  |  | 1 | 60 | 60 | I60/1
I60/2 | Incandescent | Standard Incandescent | I60 | Incandescent, (2) 60W lamp |  |  |  | 2 | 60 | 120 | I60/2
I60/3 | Incandescent | Standard Incandescent | I60 | Incandescent, (3) 60W lamp |  |  |  | 3 | 60 | 180 | I60/3
I60/4 | Incandescent | Standard Incandescent | I60 | Incandescent, (4) 60W lamp |  |  |  | 4 | 60 | 240 | I60/4
I60/5 | Incandescent | Standard Incandescent | I60 | Incandescent, (5) 60W lamp |  |  |  | 5 | 60 | 300 | I60/5
I60E/1 | Incandescent | Standard Incandescent | I60/ES | Incandescent, (1) 60W ES lamp |  |  |  | 1 | 52 | 52 | I60E/1
I60EL/1 | Incandescent | Standard Incandescent | I60/ES/LL | Incandescent, (1) 60W ES/LL lamp |  |  |  | 1 | 52 | 52 | I60EL/1
I65/1 | Incandescent | Standard Incandescent | I65 | Incandescent, (1) 65W lamp |  |  |  | 1 | 65 | 65 | I65/1
I65/2 | Incandescent | Standard Incandescent | I65 | Incandescent, (2) 65W lamp |  |  |  | 2 | 65 | 130 | I65/2
I67/1 | Incandescent | Standard Incandescent | I67 | Incandescent, (1) 67W lamp |  |  |  | 1 | 67 | 67 | I67/1
I67/2 | Incandescent | Standard Incandescent | I67 | Incandescent, (2) 67W lamp |  |  |  | 2 | 67 | 134 | I67/2
I67/3 | Incandescent | Standard Incandescent | I67 | Incandescent, (3) 67W lamp |  |  |  | 3 | 67 | 201 | I67/3
I69/1 | Incandescent | Standard Incandescent | I69 | Incandescent, (1) 69W lamp |  |  |  | 1 | 69 | 69 | I69/1
I7.5/1 | Incandescent | Standard Incandescent | I7.5 | Tungsten exit light, (1) 7.5 W lamp, used in night light application |  |  |  | 1 | 7.5 | 8 | I7.5/1
I7.5/2 | Incandescent | Standard Incandescent | I7.5 | Tungsten exit light, (2) 7.5 W lamp, used in night light application |  |  |  | 2 | 7.5 | 15 | I7.5/2
I72/1 | Incandescent | Standard Incandescent | I72 | Incandescent, (1) 72W lamp |  |  |  | 1 | 72 | 72 | I72/1
I75/1 | Incandescent | Standard Incandescent | I75 | Incandescent, (1) 75W lamp |  |  |  | 1 | 75 | 75 | I75/1
I75/2 | Incandescent | Standard Incandescent | I75 | Incandescent, (2) 75W lamp |  |  |  | 2 | 75 | 150 | I75/2
I75/3 | Incandescent | Standard Incandescent | I75 | Incandescent, (3) 75W lamp |  |  |  | 3 | 75 | 225 | I75/3
I75/4 | Incandescent | Standard Incandescent | I75 | Incandescent, (4) 75W lamp |  |  |  | 4 | 75 | 300 | I75/4
I750/1 | Incandescent | Standard Incandescent | I750 | Incandescent, (1) 750W lamp |  |  |  | 1 | 750 | 750 | I750/1
I75E/1 | Incandescent | Standard Incandescent | I75/ES | Incandescent, (1) 75W ES lamp |  |  |  | 1 | 67 | 67 | I75E/1
I75EL/1 | Incandescent | Standard Incandescent | I75/ES/LL | Incandescent, (1) 75W ES/LL lamp |  |  |  | 1 | 67 | 67 | I75EL/1
I80/1 | Incandescent | Standard Incandescent | I80 | Incandescent, (1) 80W lamp |  |  |  | 1 | 80 | 80 | I80/1
I85/1 | Incandescent | Standard Incandescent | I85 | Incandescent, (1) 85W lamp |  |  |  | 1 | 85 | 85 | I85/1
I90/1 | Incandescent | Standard Incandescent | I90 | Incandescent, (1) 90W lamp |  |  |  | 1 | 90 | 90 | I90/1
I90/2 | Incandescent | Standard Incandescent | I90 | Incandescent, (2) 90W lamp |  |  |  | 2 | 90 | 180 | I90/2
I90/3 | Incandescent | Standard Incandescent | I90 | Incandescent, (3) 90W lamp |  |  |  | 3 | 90 | 270 | I90/3
I93/1 | Incandescent | Standard Incandescent | I93 | Incandescent, (1) 93W lamp |  |  |  | 1 | 93 | 93 | I93/1
I95/1 | Incandescent | Standard Incandescent | I95 | Incandescent, (1) 95W lamp |  |  |  | 1 | 95 | 95 | I95/1
I95/2 | Incandescent | Standard Incandescent | I95 | Incandescent, (2) 95W lamp |  |  |  | 2 | 95 | 190 | I95/2
QL165/1 | Induction Fluorescent | Induction Fluorescent | QL165 | QL Induction, (1) 165W lamp | Generator | 1 |  | 1 | 165 | 165 | QL165/1
QL55/1 | Induction Fluorescent | Induction Fluorescent | QL55 | QL Induction, (1) 55W lamp | Generator | 1 |  | 1 | 55 | 55 | QL55/1
QL85/1 | Induction Fluorescent | Induction Fluorescent | QL85 | QL Induction, (1) 85W lamp | Generator | 1 |  | 1 | 85 | 85 | QL85/1
SLED10/1 | LED | LED Screw-In | LED 10W | Screw In - Light Emitting Diode Lamp, (1) 10W | Electronic | 1 |  | 1 | 10 | 10 | SLED10/1
SLED11/1 | LED | LED Screw-In | LED 11W | Screw In - Light Emitting Diode Lamp, (1) 11W | Electronic | 1 |  | 1 | 11 | 11 | SLED11/1
SLED12/1 | LED | LED Screw-In | LED 12W | Screw In - Light Emitting Diode Lamp, (1) 12W | Electronic | 1 |  | 1 | 12 | 12 | SLED12/1
SLED13/1 | LED | LED Screw-In | LED 13W | Screw In - Light Emitting Diode Lamp, (1) 13W | Electronic | 1 |  | 1 | 13 | 13 | SLED13/1
SLED14/1 | LED | LED Screw-In | LED 14W | Screw In - Light Emitting Diode Lamp, (1) 14W | Electronic | 1 |  | 1 | 14 | 14 | SLED14/1
SLED15/1 | LED | LED Screw-In | LED 15W | Screw In - Light Emitting Diode Lamp, (1) 15W | Electronic | 1 |  | 1 | 15 | 15 | SLED15/1
SLED16/1 | LED | LED Screw-In | LED 16W | Screw In - Light Emitting Diode Lamp, (1) 16W | Electronic | 1 |  | 1 | 16 | 16 | SLED16/1
SLED17/1 | LED | LED Screw-In | LED 17W | Screw In - Light Emitting Diode Lamp, (1) 17W | Electronic | 1 |  | 1 | 17 | 17 | SLED17/1
SLED18/1 | LED | LED Screw-In | LED 18W | Screw In - Light Emitting Diode Lamp, (1) 18W | Electronic | 1 |  | 1 | 18 | 18 | SLED18/1
SLED19/1 | LED | LED Screw-In | LED 19W | Screw In - Light Emitting Diode Lamp, (1) 19W | Electronic | 1 |  | 1 | 19 | 19 | SLED19/1
SLED2/1 | LED | LED Screw-In | LED 2W | Screw In - Light Emitting Diode Lamp, (1) 2W | Electronic | 1 |  | 1 | 2 | 2 | SLED2/1
SLED20/1 | LED | LED Screw-In | LED 20W | Screw In - Light Emitting Diode Lamp, (1) 20W | Electronic | 1 |  | 1 | 20 | 20 | SLED20/1
SLED21/1 | LED | LED Screw-In | LED 21W | Screw In - Light Emitting Diode Lamp, (1) 21W | Electronic | 1 |  | 1 | 21 | 21 | SLED21/1
SLED22/1 | LED | LED Screw-In | LED 22W | Screw In - Light Emitting Diode Lamp, (1) 22W | Electronic | 1 |  | 1 | 22 | 22 | SLED22/1
SLED26/1 | LED | LED Screw-In | LED 26W | Screw In - Light Emitting Diode Lamp, (1) 26W | Electronic | 1 |  | 1 | 26 | 26 | SLED26/1
SLED3/1 | LED | LED Screw-In | LED 3W | Screw In - Light Emitting Diode Lamp, (1) 3W | Electronic | 1 |  | 1 | 3 | 3 | SLED3/1
SLED4/1 | LED | LED Screw-In | LED 4W | Screw In - Light Emitting Diode Lamp, (1) 4W | Electronic | 1 |  | 1 | 4 | 4 | SLED4/1
SLED5/1 | LED | LED Screw-In | LED 5W | Screw In - Light Emitting Diode Lamp, (1) 5W | Electronic | 1 |  | 1 | 5 | 5 | SLED5/1
SLED6/1 | LED | LED Screw-In | LED 6W | Screw In - Light Emitting Diode Lamp, (1) 6W | Electronic | 1 |  | 1 | 6 | 6 | SLED6/1
SLED7/1 | LED | LED Screw-In | LED 7W | Screw In - Light Emitting Diode Lamp, (1) 7W | Electronic | 1 |  | 1 | 7 | 7 | SLED7/1
SLED8/1 | LED | LED Screw-In | LED 8W | Screw In - Light Emitting Diode Lamp, (1) 8W | Electronic | 1 |  | 1 | 8 | 8 | SLED8/1
SLED9/1 | LED | LED Screw-In | LED 9W | Screw In - Light Emitting Diode Lamp, (1) 9W | Electronic | 1 |  | 1 | 9 | 9 | SLED9/1
F1.51LS | Linear Fluorescent | T8 Linear Fluorescent | F15T8 | Fluorescent, (1) 18" T8 lamp | Mag-STD | 1 | 12 | 1 | 15 | 19 | F1.51LS
F1.51SS | Linear Fluorescent | T12 Linear Fluorescent | F15T12 | Fluorescent, (1) 18" T12 lamp | Mag-STD | 1 | 12 | 1 | 15 | 19 | F1.51LS
F1.52LS | Linear Fluorescent | T8 Linear Fluorescent | F15T8 | Fluorescent, (2) 18" T8 lamp | Mag-STD | 1 | 12 | 2 | 15 | 36 | F1.52LS
F1.52SS | Linear Fluorescent | T12 Linear Fluorescent | F15T12 | Fluorescent, (2) 18", T12 lamp | Mag-STD | 1 | 12 | 2 | 15 | 36 | F1.52LS
F21GHL | Linear Fluorescent | T5 Linear Fluorescent | F24T5/HO | Fluorescent, (1) 24", STD HO T5 lamp | Electronic | 1 | 24 | 1 | 24 | 29 | F21GHL
F21GL | Linear Fluorescent | T5 Linear Fluorescent | F24T5 | Fluorescent, (1) 24", STD T5 lamp | Electronic | 1 | 24 | 1 | 14 | 18 | F21GL
F21HS | Linear Fluorescent | T12 Linear Fluorescent | F24T12/HO | Fluorescent, (1) 24", HO lamp | Mag-STD | 1 | 24 | 1 | 35 | 62 | F21ILL
F21ILL | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 24 | 1 | 17 | 20 | F21ILL
F21ILL/T2 | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 24 | 1 | 17 | 17 | F21ILL/T2
F21ILL/T2-R | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, RLO (BF<.85), Tandem 2 Lamp Ballast | Electronic | 1 | 24 | 1 | 17 | 15 | F21ILL/T2-R
F21ILL/T3 | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 1 | 24 | 1 | 17 | 16 | F21ILL/T3
F21ILL/T3-R | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, RLO (BF<.85), Tandem 3 Lamp Ballast | Electronic | 1 | 24 | 1 | 17 | 14 | F21ILL/T3-R
F21ILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 1 | 24 | 1 | 17 | 15 | F21ILL/T4
F21ILL/T4-R | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, RLO (BF<.85), Tandem 4 Lamp Ballast | Electronic | 1 | 24 | 1 | 17 | 14 | F21ILL/T4-R
F21LL | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (1) 24", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 24 | 1 | 17 | 16 | F21LL
F21LL/T2 | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (1) 24", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 24 | 1 | 17 | 16 | F21LL/T2
F21LL/T3 | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (1) 24", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 1 | 24 | 1 | 17 | 17 | F21LL/T3
F21LL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (1) 24", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 1 | 24 | 1 | 17 | 17 | F21LL/T4
F21LL-R | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (1) 24", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 1 | 24 | 1 | 17 | 15 | F21LL-R
F21LS | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (1) 24", T8 lamp, Standard Ballast | Mag-STD | 1 | 24 | 1 | 17 | 24 | F21LS
F21SE | Linear Fluorescent | T12 Linear Fluorescent | F20T12 | Fluorescent, (1) 24", STD lamp | Mag-ES | 1 | 24 | 1 | 20 | 26 | F21ILL
F21SS | Linear Fluorescent | T12 Linear Fluorescent | F20T12 | Fluorescent, (1) 24", STD lamp | Mag-STD | 1 | 24 | 1 | 20 | 28 | F21ILL
F22GHL | Linear Fluorescent | T5 Linear Fluorescent | F24T5/HO | Fluorescent, (2) 24", STD HO T5 lamp | Electronic | 1 | 24 | 2 | 24 | 55 | F22GHL
F22GL | Linear Fluorescent | T5 Linear Fluorescent | F24T5 | Fluorescent, (2) 24", STD T5 lamp | Electronic | 1 | 24 | 2 | 14 | 35 | F22GL
F22ILE | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (2) 24", T-8 Instant Start lamp, Energy Saving Magnetic Ballast | Mag-ES | 1 | 24 | 2 | 17 | 45 | F22ILE
F22ILL | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (2) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 24 | 2 | 17 | 33 | F22ILL
F22ILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (2) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 1 | 24 | 2 | 17 | 31 | F22ILL/T4
F22ILL/T4-R | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (2) 24", T-8 lamp, Instant Start Ballast, RLO (BF<.85), Tandem 4 Lamp Ballast | Electronic | 1 | 24 | 2 | 17 | 28 | F22ILL/T4-R
F22ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (2) 24", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 1 | 24 | 2 | 17 | 29 | F22ILL-R
F22LL | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (2) 24", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 24 | 2 | 17 | 31 | F22LL
F22LL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (2) 24", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 1 | 24 | 2 | 17 | 34 | F22LL/T4
F22LL-R | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (2) 24", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 1 | 24 | 2 | 17 | 28 | F22LL-R
F22SE | Linear Fluorescent | T12 Linear Fluorescent | F20T12 | Fluorescent, (2) 24", STD lamp | Mag-ES | 1 | 24 | 2 | 20 | 51 | F22ILL
F22SHS | Linear Fluorescent | T12 Linear Fluorescent | F24T12/HO | Fluorescent, (2) 24", HO lamp | Mag-STD | 1 | 24 | 2 | 35 | 90 | F22ILL
F22SS | Linear Fluorescent | T12 Linear Fluorescent | F20T12 | Fluorescent, (2) 24", STD lamp | Mag-STD | 1 | 24 | 2 | 20 | 56 | F22ILL
F23ILL | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (3) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 24 | 3 | 17 | 47 | F23ILL
F23ILL-H | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (3) 24", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 1 | 24 | 3 | 17 | 49 | F23ILL-H
F23ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (3) 24", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 1 | 24 | 3 | 17 | 43 | F23ILL-R
F23LL | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (3) 24", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 24 | 3 | 17 | 52 | F23LL
F23LL-R | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (3) 24", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 1 | 24 | 3 | 17 | 41 | F23LL-R
F23SE | Linear Fluorescent | T12 Linear Fluorescent | F20T12 | Fluorescent, (3) 24", STD lamp | Mag-ES | 1 | 24 | 3 | 20 | 77 | F23ILL
F23SS | Linear Fluorescent | T12 Linear Fluorescent | F20T12 | Fluorescent, (3) 24", STD lamp | Mag-STD | 1 | 24 | 3 | 20 | 84 | F23ILL
F24ILL | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (4) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 24 | 4 | 17 | 61 | F24ILL
F24ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (4) 24", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 1 | 24 | 4 | 17 | 55 | F24ILL-R
F24LL | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (4) 24", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 24 | 4 | 17 | 68 | F24LL
F24LL-R | Linear Fluorescent | T8 Linear Fluorescent | F17T8 | Fluorescent, (4) 24", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 1 | 24 | 4 | 17 | 57 | F24LL-R
F24SE | Linear Fluorescent | T12 Linear Fluorescent | F20T12 | Fluorescent, (4) 24", STD lamp | Mag-ES | 1 | 24 | 4 | 20 | 102 | F24ILL
F24SS | Linear Fluorescent | T12 Linear Fluorescent | F20T12 | Fluorescent, (4) 24", STD lamp | Mag-STD | 1 | 24 | 4 | 20 | 112 | F24ILL
F26SE | Linear Fluorescent | T12 Linear Fluorescent | F20T12 | Fluorescent, (6) 24", STD lamp | Mag-ES | 1 | 24 | 6 | 20 | 153 | F26ILL
F26SS | Linear Fluorescent | T12 Linear Fluorescent | F20T12 | Fluorescent, (6) 24", STD lamp | Mag-STD | 1 | 24 | 6 | 20 | 168 | F26ILL
F31EE | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (1) 36", ES lamp | Mag-ES | 1 | 36 | 1 | 25 | 38 | F31ILL
F31EE/T2 | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (1) 36", ES lamp, Tandem wired | Mag-ES | 1 | 36 | 1 | 25 | 33 | F31ILL
F31EL | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (1) 36", ES lamp | Electronic | 1 | 36 | 1 | 25 | 26 | F31ILL
F31ES | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (1) 36", ES lamp | Mag-STD | 1 | 36 | 1 | 25 | 42 | F31ILL
F31ES/T2 | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (1) 36", ES lamp, Tandem wired | Mag-STD | 1 | 36 | 1 | 25 | 37 | F31ILL
F31GHL | Linear Fluorescent | T5 Linear Fluorescent | F36T5/HO | Fluorescent, (1) 36", STD HO T5 lamp | Electronic | 1 | 36 | 1 | 39 | 43 | F31GHL
F31GL | Linear Fluorescent | T5 Linear Fluorescent | F36T5 | Fluorescent, (1) 36", STD T5 lamp | Electronic | 1 | 36 | 1 | 21 | 27 | F31GL
F31ILL | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 36 | 1 | 25 | 26 | F31ILL
F31ILL/T2 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 36 | 1 | 25 | 23 | F31ILL/T2
F31ILL/T2-H | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, HLO (BF: .96-1.1), Tandem 2 Lamp Ballast | Electronic | 1 | 36 | 1 | 25 | 24 | F31ILL/T2-H
F31ILL/T2-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, RLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 36 | 1 | 25 | 23 | F31ILL/T2-R
F31ILL/T3 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 1 | 36 | 1 | 25 | 22 | F31ILL/T3
F31ILL/T3-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, RLO (BF<.85), Tandem 3 Lamp Ballast | Electronic | 1 | 36 | 1 | 25 | 22 | F31ILL/T3-R
F31ILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 1 | 36 | 1 | 25 | 22 | F31ILL/T4
F31ILL/T4-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, RLO (BF<.85), Tandem 4 Lamp Ballast | Electronic | 1 | 36 | 1 | 25 | 22 | F31ILL/T4-R
F31ILL-H | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 1 | 36 | 1 | 25 | 28 | F31ILL-H
F31ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 1 | 36 | 1 | 25 | 27 | F31ILL-R
F31LL | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 36 | 1 | 25 | 24 | F31LL
F31LL/T2 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 36 | 1 | 25 | 23 | F31LL/T2
F31LL/T3 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 1 | 36 | 1 | 25 | 24 | F31LL/T3
F31LL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 1 | 36 | 1 | 25 | 22 | F31LL/T4
F31LL-H | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Rapid Start Ballast, HLO (BF:.96-1.1) | Electronic | 1 | 36 | 1 | 25 | 26 | F31LL-H
F31LL-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 36", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 1 | 36 | 1 | 25 | 23 | F31LL-R
F31SE/T2 | Linear Fluorescent | T12 Linear Fluorescent | F30T12 | Fluorescent, (1) 36", STD lamp, Tandem wired | Mag-ES | 1 | 36 | 1 | 30 | 37 | F31ILL
F31SHS | Linear Fluorescent | T12 Linear Fluorescent | F36T12/HO | Fluorescent, (1) 36", HO lamp | Mag-STD | 1 | 36 | 1 | 50 | 70 | F31ILL
F31SL | Linear Fluorescent | T12 Linear Fluorescent | F30T12 | Fluorescent, (1) 36", STD lamp | Electronic | 1 | 36 | 1 | 30 | 31 | F31ILL
F31SS | Linear Fluorescent | T12 Linear Fluorescent | F30T12 | Fluorescent, (1) 36", STD lamp | Mag-STD | 1 | 36 | 1 | 30 | 46 | F31ILL
F31SS/T2 | Linear Fluorescent | T12 Linear Fluorescent | F30T12 | Fluorescent, (1) 36", STD lamp, Tandem wired | Mag-STD | 1 | 36 | 1 | 30 | 41 | F31ILL
F32EE | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (2) 36", ES lamp | Mag-ES | 1 | 36 | 2 | 25 | 66 | F32ILL
F32EL | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (2) 36", ES lamp | Electronic | 1 | 36 | 2 | 25 | 50 | F32ILL
F32ES | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (2) 36", ES lamp | Mag-STD | 1 | 36 | 2 | 25 | 73 | F32ILL
F32GHL | Linear Fluorescent | T5 Linear Fluorescent | F36T5/HO | Fluorescent, (2) 36", STD HO T5 lamp | Electronic | 1 | 36 | 2 | 39 | 85 | F32GHL
F32GL | Linear Fluorescent | T5 Linear Fluorescent | F36T5 | Fluorescent, (1) 36", STD T5 lamp | Electronic | 1 | 36 | 2 | 21 | 52 | F32GL
F32ILL | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 36 | 2 | 25 | 46 | F32ILL
F32ILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 1 | 36 | 2 | 25 | 44 | F32ILL/T4
F32ILL/T4-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 36", T-8 lamp, Instant Start Ballast, RLO (BF<.85), Tandem 4 Lamp Ballast | Electronic | 1 | 36 | 2 | 25 | 43 | F32ILL/T4-R
F32ILL-H | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 36", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 1 | 36 | 2 | 25 | 48 | F32ILL-H
F32ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 36", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 1 | 36 | 2 | 25 | 46 | F32ILL-R
F32LE | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 36", T-8 lamp | Mag-ES | 1 | 36 | 2 | 25 | 65 | F32LE
F32LL | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 36", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 36 | 2 | 25 | 46 | F32LL
F32LL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 36", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 1 | 36 | 2 | 25 | 45 | F32LL/T4
F32LL-H | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 36", T-8 lamp, Rapid Start Ballast, HLO (BF:.96-1.1) | Electronic | 1 | 36 | 2 | 25 | 50 | F32LL-H
F32LL-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 36", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 1 | 36 | 2 | 25 | 42 | F32LL-R
F32LL-V | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 36", T-8 lamp, Rapid Start Ballast, VHLO (BF>1.1) | Electronic | 1 | 36 | 2 | 25 | 70 | F32LL-V
F32SE | Linear Fluorescent | T12 Linear Fluorescent | F30T12 | Fluorescent, (2) 36", STD lamp | Mag-ES | 1 | 36 | 2 | 30 | 74 | F32ILL
F32SHS | Linear Fluorescent | T5 Linear Fluorescent | F36T12/HO | Fluorescent, (2) 36", HO, lamp | Mag-STD | 1 | 36 | 2 | 50 | 114 | F32SHS
F32SL | Linear Fluorescent | T12 Linear Fluorescent | F30T12 | Fluorescent, (2) 36", STD lamp | Electronic | 1 | 36 | 2 | 30 | 58 | F32ILL
F32SS | Linear Fluorescent | T12 Linear Fluorescent | F30T12 | Fluorescent, (2) 36", STD lamp | Mag-STD | 1 | 36 | 2 | 30 | 81 | F32ILL
F33EE | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (3) 36", ES lamp | Mag-ES | 1 | 36 | 3 | 25 | 104 | F33ILL
F33EL | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (3) 36", ES lamp | Electronic | 1 | 36 | 3 | 25 | 76 | F33ILL
F33ES | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (3) 36", ES lamp | Mag-STD | 1 | 36 | 3 | 25 | 115 | F33ILL
F33ILL | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (3) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 36 | 3 | 25 | 67 | F33ILL
F33ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (3) 36", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 1 | 36 | 3 | 25 | 66 | F33ILL-R
F33LL | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (3) 36", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 36 | 3 | 25 | 72 | F33LL
F33LL-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (3) 36", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 1 | 36 | 3 | 25 | 62 | F33LL-R
F33SE | Linear Fluorescent | T12 Linear Fluorescent | F30T12 | Fluorescent, (3) 36", STD lamp, (1) STD ballast and (1) ES ballast | Mag-ES | 1 | 36 | 3 | 30 | 120 | F33ILL
F33SS | Linear Fluorescent | T12 Linear Fluorescent | F30T12 | Fluorescent, (3) 36", STD lamp | Mag-STD | 1 | 36 | 3 | 30 | 127 | F33ILL
F34EE | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (4) 36", ES lamp | Mag-ES | 1 | 36 | 4 | 25 | 132 | F34ILL
F34EL | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (4) 36", ES lamp | Electronic | 1 | 36 | 4 | 25 | 100 | F34ILL
F34ILL | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (4) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 36 | 4 | 25 | 87 | F34ILL
F34ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (4) 36", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 1 | 36 | 4 | 25 | 86 | F34ILL-R
F34LL | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (4) 36", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 36 | 4 | 25 | 89 | F34LL
F34LL-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (4) 36", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 1 | 36 | 4 | 25 | 84 | F34LL-R
F34SE | Linear Fluorescent | T12 Linear Fluorescent | F30T12 | Fluorescent, (4) 36", STD lamp | Mag-ES | 1 | 36 | 4 | 30 | 148 | F34ILL
F34SL | Linear Fluorescent | T12 Linear Fluorescent | F30T12 | Fluorescent, (4) 36", STD lamp | Electronic | 1 | 36 | 4 | 30 | 116 | F34ILL
F34SS | Linear Fluorescent | T12 Linear Fluorescent | F30T12 | Fluorescent, (4) 36", STD lamp | Mag-STD | 1 | 36 | 4 | 30 | 162 | F34ILL
F36EE | Linear Fluorescent | T12 Linear Fluorescent | F30T12/ES | Fluorescent, (6) 36", ES lamp | Mag-ES | 1 | 36 | 6 | 25 | 198 | F36ILL
F36ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (6) 36", T-8 lamp, Instant Start Ballast, RLO (BF<.85) | Electronic | 1 | 36 | 6 | 25 | 134 | F36ILL-R
F36SE | Linear Fluorescent | T12 Linear Fluorescent | F30T12 | Fluorescent, (6) 36", STD lamp | Mag-ES | 1 | 36 | 6 | 30 | 238 | F36ILL
F410GHL | Linear Fluorescent | T8 Linear Fluorescent | F48T5/HO | Fluorescent, (10) 48", STD HO T5 lamp | Electronic | 1 | 48 | 10 | 54 | 588 | F410GHL
F412GHL | Linear Fluorescent | T8 Linear Fluorescent | F48T5/HO | Fluorescent, (12) 48", STD HO T5 lamp | Electronic | 1 | 48 | 12 | 54 | 702 | F412GHL
F41EE | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (1) 48", ES lamp | Mag-ES | 1 | 48 | 1 | 34 | 43 | F41ILL
F41EE/D2 | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (1) 48", ES lamp, 2 ballast | Mag-ES | 2 | 48 | 1 | 34 | 43 | F41ILL
F41EE/T2 | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (1) 48", ES lamp, tandem wired, 2-lamp ballast | Mag-ES | 1 | 48 | 1 | 34 | 36 | F41ILL
F41EHS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/HO/ES | Fluorescent, (1) 48", ES HO lamp | Mag-STD | 1 | 48 | 1 | 55 | 80 | F41ILL
F41EIS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/ES | Fluorescent, (1) 48" ES Instant Start lamp. Magnetic ballast | Mag-STD | 1 | 48 | 1 | 30 | 51 | F41ILL
F41EL | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (1) 48", T12 ES lamp, Electronic Ballast | Electronic | 1 | 48 | 1 | 34 | 32 | F41ILL
F41EL/T2 | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (1) 48", T-12 ES lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 48 | 1 | 34 | 32 | F41ILL
F41ES | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (1) 48", ES lamp | Mag-STD | 1 | 48 | 1 | 34 | 50 | F41ILL
F41EVS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/VHO/ES | Fluorescent, (1) 48", VHO ES lamp | Mag-STD | 1 | 48 | 1 |  | 123 | F41ILL
F41GHL | Linear Fluorescent | T5 Linear Fluorescent | F48T5/HO | Fluorescent, (1) 48", STD HO T5 lamp | Electronic | 1 | 48 | 1 | 54 | 59 | F41GHL
F41GHL-H | Linear Fluorescent | T5 Linear Fluorescent | F54T5/HO | Fluorescent, (1) 48", STD HO T5 lamp HLO (BF: .96-1.2) | Electronic | 1 | 48 | 1 | 54 | 62 | F41GHL-H
F41GL | Linear Fluorescent | T5 Linear Fluorescent | F48T5 | Fluorescent, (1) 48", STD T5 lamp | Electronic | 1 | 48 | 1 | 28 | 32 | F41GL
F41IAL | Linear Fluorescent | T12 Linear Fluorescent | F25T12 | Fluorescent, (1) 48", F25T12 lamp, Instant Start Ballast | Electronic | 1 | 48 | 1 | 25 | 25 | F41ILL
F41IAL/T2-R | Linear Fluorescent | T12 Linear Fluorescent | F25T12 | Fluorescent, (1) 48", F25T12 lamp, Instant Start, Tandem 2-Lamp Ballast, RLO (BF<0.85) | Electronic | 1 | 48 | 1 | 25 | 19 | F41ILL
F41IAL/T3-R | Linear Fluorescent | T12 Linear Fluorescent | F25T12 | Fluorescent, (1) 48", F25T12 lamp, Instant Start, Tandem 3-Lamp Ballast, RLO (BF<0.85) | Electronic | 1 | 48 | 1 | 25 | 20 | F41ILL
F41ILL | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 48 | 1 | 32 | 31 | F41ILL
F41ILL/T2 | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 48 | 1 | 32 | 30 | F41ILL/T2
F41ILL/T2-H | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1), Tandem 2 Lamp Ballast | Electronic | 1 | 48 | 1 | 32 | 33 | F41ILL/T2-H
F41ILL/T2-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 2 Lamp Ballast | Electronic | 1 | 48 | 1 | 32 | 26 | F41ILL/T2-R
F41ILL/T3 | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 1 | 48 | 1 | 32 | 30 | F41ILL/T3
F41ILL/T3-H | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1), Tandem 3 Lamp Ballast | Electronic | 1 | 48 | 1 | 32 | 31 | F41ILL/T3-H
F41ILL/T3-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 3 Lamp Ballast | Electronic | 1 | 48 | 1 | 32 | 26 | F41ILL/T3-R
F41ILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 1 | 48 | 1 | 32 | 28 | F41ILL/T4
F41ILL/T4-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 1 | 48 | 1 | 32 | 26 | F41ILL/T4-R
F41ILL-H | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 1 | 48 | 1 | 32 | 36 | F41ILL-H
F41LE | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp | Mag-ES | 1 | 48 | 1 | 32 | 35 | F41LE
F41LL | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 48 | 1 | 32 | 32 | F41LL
F41LL/T2 | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 48 | 1 | 32 | 30 | F41LL/T2
F41LL/T2-H | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, HLO (BF:.96-1.1), Tandem 2 Lamp Ballast | Electronic | 1 | 48 | 1 | 32 | 39 | F41LL/T2-H
F41LL/T2-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85), Tandem 2 Lamp Ballast | Electronic | 1 | 48 | 1 | 32 | 27 | F41LL/T2-R
F41LL/T3 | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 1 | 48 | 1 | 32 | 31 | F41LL/T3
F41LL/T3-H | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, HLO (BF:.96-1.1), Tandem 3 Lamp Ballast | Electronic | 1 | 48 | 1 | 32 | 33 | F41LL/T3-H
F41LL/T3-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85), Tandem 3 Lamp Ballast | Electronic | 1 | 48 | 1 | 32 | 25 | F41LL/T3-R
F41LL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 1 | 48 | 1 | 32 | 30 | F41LL/T4
F41LL/T4-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 1 | 48 | 1 | 32 | 26 | F41LL/T4-R
F41LL-H | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, HLO (BF:.96-1.1) | Electronic | 1 | 48 | 1 | 32 | 39 | F41LL-H
F41LL-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 1 | 48 | 1 | 32 | 27 | F41LL-R
F41RSILL | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 48", 25W T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 48 | 1 | 25 | 22 | F41RSILL
F41RSILL/T2 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 48", 25W T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 48 | 1 | 25 | 22 | F41RSILL/T2
F41RSILL/T3 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 48", 25W T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 1 | 48 | 1 | 25 | 22 | F41RSILL/T3
F41RSILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 48", 25W T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 1 | 48 | 1 | 25 | 22 | F41RSILL/T4
F41RSILL-H | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 48", 25W T-8 lamp, Instant Start Ballast, HLO (BF:.96 - 1.2) | Electronic | 1 | 48 | 1 | 25 | 30 | F41RSILL-H
F41RSILL-H/T2 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 48", 25W T-8 lamp, Instant Start Ballast, HLO (BF:.96 - 1.2), Tandem 2 Lamp Ballast | Electronic | 1 | 48 | 1 | 25 | 30 | F41RSILL-H/T2
F41RSILL-H/T3 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 48", 25W T-8 lamp, Instant Start Ballast, HLO (BF:.96 - 1.2), Tandem 3 Lamp Ballast | Electronic | 1 | 48 | 1 | 25 | 30 | F41RSILL-H/T3
F41RSILL-H/T4 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 48", 25W T-8 lamp, Instant Start Ballast, HLO (BF:.96 - 1.2), Tandem 4 Lamp Ballast | Electronic | 1 | 48 | 1 | 25 | 29 | F41RSILL-H/T4
F41RSILL-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 48", 25W T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 1 | 48 | 1 | 25 | 20 | F41RSILL-R
F41RSILL-R/T2 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 48", 25W T-8 lamp, Instant Start Ballast, RLO (BF<0.85), Tandem 2 Lamp Ballast | Electronic | 1 | 48 | 1 | 25 | 19 | F41RSILL-R/T2
F41RSILL-R/T3 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 48", 25W T-8 lamp, Instant Start Ballast, RLO (BF<0.85), Tandem 3 Lamp Ballast | Electronic | 1 | 48 | 1 | 25 | 19 | F41RSILL-R/T3
F41RSILL-R/T4 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (1) 48", 25W T-8 lamp, Instant Start Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 1 | 48 | 1 | 25 | 19 | F41RSILL-R/T4
F41SE | Linear Fluorescent | T12 Linear Fluorescent | F40T12 | Fluorescent, (1) 48", STD lamp | Mag-ES | 1 | 48 | 1 | 40 | 50 | F41ILL
F41SHS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/HO | Fluorescent, (1) 48", STD HO lamp | Mag-STD | 1 | 48 | 1 | 60 | 85 | F41ILL
F41SIL | Linear Fluorescent | T12 Linear Fluorescent | F48T12 | Fluorescent, (1) 48", STD IS lamp, Electronic ballast | Electronic | 1 | 48 | 1 | 39 | 46 | F41ILL
F41SIL/T2 | Linear Fluorescent | T12 Linear Fluorescent | F48T12 | Fluorescent, (1) 48", STD IS lamp, Electronic ballast, tandem wired | Electronic | 1 | 48 | 1 | 39 | 37 | F41ILL
F41SILL | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 48 | 1 | 30 | 28 | F41SILL
F41SILL/T2 | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 48 | 1 | 30 | 27 | F41SILL/T2
F41SILL/T2-H | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1), Tandem 2 Lamp Ballast | Electronic | 1 | 48 | 1 | 30 | 36 | F41SILL/T2-H
F41SILL/T2-R | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 2 Lamp Ballast | Electronic | 1 | 48 | 1 | 30 | 24 | F41SILL/T2-R
F41SILL/T3 | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 1 | 48 | 1 | 30 | 27 | F41SILL/T3
F41SILL/T3-H | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1), Tandem 3 Lamp Ballast | Electronic | 1 | 48 | 1 | 30 | 36 | F41SILL/T3-H
F41SILL/T3-R | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 3 Lamp Ballast | Electronic | 1 | 48 | 1 | 30 | 24 | F41SILL/T3-R
F41SILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 1 | 48 | 1 | 30 | 26 | F41SILL/T4
F41SILL/T4-R | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 1 | 48 | 1 | 30 | 23 | F41SILL/T4-R
F41SILL-H | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 1 | 48 | 1 | 30 | 37 | F41SILL-H
F41SILL-R | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 1 | 48 | 1 | 30 | 25 | F41SILL-R
F41SIS | Linear Fluorescent | T12 Linear Fluorescent | F48T12 | Fluorescent, (1) 48", STD IS lamp | Mag-STD | 1 | 48 | 1 | 39 | 60 | F41ILL
F41SIS/T2 | Linear Fluorescent | T12 Linear Fluorescent | F48T12 | Fluorescent, (1) 48", STD IS lamp, tandem to 2-lamp ballast | Mag-STD | 1 | 48 | 1 | 39 | 52 | F41ILL
F41SL/T2 | Linear Fluorescent | T12 Linear Fluorescent | F40T12 | Fluorescent, (1) 48", T-12 STD lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 48 | 1 | 40 | 36 | F41ILL
F41SS | Linear Fluorescent | T12 Linear Fluorescent | F40T12 | Fluorescent, (1) 48", STD lamp | Mag-STD | 1 | 48 | 1 | 40 | 57 | F41ILL
F41SSILL | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 48 | 1 | 28 | 26 | F41SSILL
F41SSILL/T2 | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 48 | 1 | 28 | 25 | F41SSILL/T2
F41SSILL/T2-H | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1), Tandem 2 Lamp Ballast | Electronic | 1 | 48 | 1 | 28 | 32 | F41SSILL/T2-H
F41SSILL/T2-R | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 2 Lamp Ballast | Electronic | 1 | 48 | 1 | 28 | 22 | F41SSILL/T2-R
F41SSILL/T3 | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 1 | 48 | 1 | 28 | 25 | F41SSILL/T3
F41SSILL/T3-H | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1), Tandem 3 Lamp Ballast | Electronic | 1 | 48 | 1 | 28 | 32 | F41SSILL/T3-H
F41SSILL/T3-R | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 3 Lamp Ballast | Electronic | 1 | 48 | 1 | 28 | 22 | F41SSILL/T3-R
F41SSILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 1 | 48 | 1 | 28 | 24 | F41SSILL/T4
F41SSILL/T4-R | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 1 | 48 | 1 | 28 | 21 | F41SSILL/T4-R
F41SSILL-H | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 1 | 48 | 1 | 28 | 33 | F41SSILL-H
F41SSILL-R | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (1) 48", Super T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 1 | 48 | 1 | 28 | 23 | F41SSILL-R
F41SVS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/VHO | Fluorescent, (1) 48", STD VHO lamp | Mag-STD | 1 | 48 | 1 | 110 | 135 | F41ILL
F41TS | Linear Fluorescent | T10 Linear Fluorescent | F40T10 | Fluorescent, (1) 48", T-10 lamp | Mag-STD | 1 | 48 | 1 | 40 | 51 | F41ILL
F42EE | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (2) 48", ES lamp | Mag-ES | 1 | 48 | 2 | 34 | 72 | F42ILL
F42EE/D2 | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (2) 48", ES lamp, 2 Ballasts (delamped) | Mag-ES | 2 | 48 | 2 | 34 | 76 | F42ILL
F42EHS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/HO/ES | Fluorescent, (2) 42", HO lamp (3.5' lamp) | Mag-STD | 1 | 48 | 2 | 55 | 135 | F42ILL
F42EIS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/ES | Fluorescent, (2) 48" ES Instant Start lamp. Magnetic ballast | Mag-STD | 1 | 48 | 2 | 30 | 82 | F42ILL
F42EL | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (2) 48", T12 ES lamps, Electronic Ballast | Electronic | 1 | 48 | 2 | 34 | 60 | F42ILL
F42ES | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (2) 48", ES lamp | Mag-STD | 1 | 48 | 2 | 34 | 80 | F42ILL
F42EVS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/VHO/ES | Fluorescent, (2) 48", VHO ES lamp | Mag-STD | 1 | 48 | 2 |  | 210 | F42ILL
F42GHL | Linear Fluorescent | T5 Linear Fluorescent | F48T5/HO | Fluorescent, (2) 48", STD HO T5 lamp | Electronic | 1 | 48 | 2 | 54 | 117 | F42GHL
F42GHL-H | Linear Fluorescent | T5 Linear Fluorescent | F54T5/HO | Fluorescent, (2) 48", STD HO T5 lamp HLO (BF: .96-1.2) | Electronic | 1 | 48 | 2 | 54 | 118 | F42GHL-H
F42GL | Linear Fluorescent | T12 Linear Fluorescent | F48T5 | Fluorescent, (2) 48", STD T5 lamp | Electronic | 1 | 48 | 2 | 28 | 63 | F42ILL
F42IAL/T4-R | Linear Fluorescent | T12 Linear Fluorescent | F25T12 | Fluorescent, (2) 48", F25T12 lamp, Instant Start, Tandem 4-Lamp Ballast, RLO (BF<0.85) | Electronic | 1 | 48 | 2 | 25 | 40 | F42ILL
F42IAL-R | Linear Fluorescent | T12 Linear Fluorescent | F25T12 | Fluorescent, (2) 48", F25T12 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 1 | 48 | 2 | 25 | 39 | F42ILL
F42ILL | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (2) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 48 | 2 | 32 | 59 | F42ILL
F42ILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (2) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 1 | 48 | 2 | 32 | 56 | F42ILL/T4
F42ILL/T4-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (2) 48", T-8 lamp, Instant Start Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 1 | 48 | 2 | 32 | 51 | F42ILL/T4-R
F42ILL-H | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (2) 48", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 1 | 48 | 2 | 32 | 65 | F42ILL-H
F42ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (2) 48", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 1 | 48 | 2 | 32 | 52 | F42ILL-R
F42ILL-V | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (2) 48", T-8 lamp, Instant Start Ballast, VHLO (BF>1.1) | Electronic | 1 | 48 | 2 | 32 | 79 | F42ILL-V
F42LE | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (2) 48", T-8 lamp | Mag-ES | 1 | 48 | 2 | 32 | 71 | F42LE
F42LL | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (2) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 48 | 2 | 32 | 60 | F42LL
F42LL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (2) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 1 | 48 | 2 | 32 | 59 | F42LL/T4
F42LL/T4-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (2) 48", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 1 | 48 | 2 | 32 | 53 | F42LL/T4-R
F42LL-H | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (2) 48", T-8 lamp, Rapid Start Ballast, HLO (BF:.96-1.1) | Electronic | 1 | 48 | 2 | 32 | 70 | F42LL-H
F42LL-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (2) 48", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 1 | 48 | 2 | 32 | 54 | F42LL-R
F42LL-V | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (2) 48", T-8 lamp, Rapid Start Ballast, VHLO (BF>1.1) | Electronic | 1 | 48 | 2 | 32 | 85 | F42LL-V
F42RSILL | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 48", 25W T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 48 | 2 | 25 | 43 | F42RSILL
F42RSILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 48", 25W T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 1 | 48 | 2 | 25 | 43 | F42RSILL/T4
F42RSILL-H | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 48", 25W T-8 lamp, Instant Start Ballast, HLO (BF:.96 - 1.2) | Electronic | 1 | 48 | 2 | 25 | 58 | F42RSILL-H
F42RSILL-H/T4 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 48", 25W T-8 lamp, Instant Start Ballast, HLO (BF:.96 - 1.2), Tandem 4 Lamp Ballast | Electronic | 1 | 48 | 2 | 25 | 58 | F42RSILL-H/T4
F42RSILL-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 48", 25W T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 1 | 48 | 2 | 25 | 38 | F42RSILL-R
F42RSILL-R/T4 | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (2) 48", 25W T-8 lamp, Instant Start Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 1 | 48 | 2 | 25 | 38 | F42RSILL-R/T4
F42SE | Linear Fluorescent | T12 Linear Fluorescent | F40T12 | Fluorescent, (2) 48", STD lamp | Mag-ES | 1 | 48 | 2 | 40 | 86 | F42ILL
F42SHS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/HO | Fluorescent, (2) 48", STD HO lamp | Mag-STD | 1 | 48 | 2 | 60 | 145 | F42ILL
F42SIL | Linear Fluorescent | T12 Linear Fluorescent | F48T12 | Fluorescent, (2) 48", STD IS lamp, Electronic ballast | Electronic | 1 | 48 | 2 | 39 | 74 | F42ILL
F42SILL | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (2) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 48 | 2 | 30 | 53 | F42SILL
F42SILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (2) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 1 | 48 | 2 | 30 | 52 | F42SILL/T4
F42SILL/T4-R | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (2) 48", Super T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 1 | 48 | 2 | 30 | 46 | F42SILL/T4-R
F42SILL-H | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (2) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-2.2) | Electronic | 1 | 48 | 2 | 30 | 72 | F42SILL-H
F42SILL-R | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (2) 48", Super T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 1 | 48 | 2 | 30 | 47 | F42SILL-R
F42SIS | Linear Fluorescent | T12 Linear Fluorescent | F48T12 | Fluorescent, (2) 48", STD IS lamp | Mag-STD | 1 | 48 | 2 | 39 | 103 | F42ILL
F42SS | Linear Fluorescent | T12 Linear Fluorescent | F40T12 | Fluorescent, (2) 48", STD lamp | Mag-STD | 1 | 48 | 2 | 40 | 94 | F42ILL
F42SSILL | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (2) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 48 | 2 | 28 | 48 | F42SSILL
F42SSILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (2) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 1 | 48 | 2 | 28 | 47 | F42SSILL/T4
F42SSILL/T4-R | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (2) 48", Super T-8 lamp, IS Ballast, RLO (BF<0.85), Tandem 4 Lamp Ballast | Electronic | 1 | 48 | 2 | 28 | 44 | F42SSILL/T4-R
F42SSILL-H | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (2) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-2.2) | Electronic | 1 | 48 | 2 | 28 | 67 | F42SSILL-H
F42SSILL-R | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (2) 48", Super T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 1 | 48 | 2 | 28 | 45 | F42SSILL-R
F42SVS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/VHO | Fluorescent, (2) 48", STD VHO lamp | Mag-STD | 1 | 48 | 2 | 110 | 242 | F42ILL
F43EE | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (3) 48", ES lamp | Mag-ES | 1 | 48 | 3 | 34 | 115 | F43ILL
F43EHS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/HO/ES | Fluorescent, (3) 48", ES HO lamp (3.5' lamp) | Mag-STD | 1 | 48 | 3 | 55 | 215 | F43ILL
F43EIS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/ES | Fluorescent, (3) 48" ES Instant Start lamp. Magnetic ballast | Mag-STD | 1 | 48 | 3 | 30 | 133 | F43ILL
F43EL | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (3) 48", T12 ES lamps, Electronic Ballast | Electronic | 1 | 48 | 3 | 34 | 92 | F43ILL
F43ES | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (3) 48", ES lamp | Mag-STD | 1 | 48 | 3 | 34 | 130 | F43ILL
F43EVS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/VHO/ES | Fluorescent, (3) 48", VHO ES lamp | Mag-STD | 1 | 48 | 3 |  | 333 | F43ILL
F43GHL | Linear Fluorescent | T5 Linear Fluorescent | F48T5/HO | Fluorescent, (3) 48", STD HO T5 lamp | Electronic | 1 | 48 | 3 | 54 | 177 | F43GHL
F43GHL-H | Linear Fluorescent | T5 Linear Fluorescent | F54T5/HO | Fluorescent, (3) 48", STD HO T5 lamp HLO (BF: .96-1.2) | Electronic | 1 | 48 | 3 | 54 | 182 | F43GHL-H
F43IAL-R | Linear Fluorescent | T12 Linear Fluorescent | F25T12 | Fluorescent, (3) 48", F25T12 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 1 | 48 | 3 | 25 | 60 | F43ILL
F43ILL | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (3) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 48 | 3 | 32 | 89 | F43ILL
F43ILL/2 | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (3) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), (2) ballast | Electronic | 2 | 48 | 3 | 32 | 90 | F43ILL/2
F43ILL-H | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (3) 48", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 1 | 48 | 3 | 32 | 93 | F43ILL-H
F43ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (3) 48", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 1 | 48 | 3 | 32 | 78 | F43ILL-R
F43ILL-V | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (3) 48", T-8 lamp, Instant Start Ballast, VHLO (BF>1.1) | Electronic | 1 | 48 | 3 | 32 | 112 | F43ILL-V
F43LE | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (3) 48", T-8 lamp | Mag-ES | 1 | 48 | 3 | 32 | 110 | F43LE
F43LL | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (3) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 48 | 3 | 32 | 93 | F43LL
F43LL/2 | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (3) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), (2) ballast | Electronic | 2 | 48 | 3 | 32 | 92 | F43LL/2
F43LL-H | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (3) 48", T-8 lamp, Rapid Start Ballast, HLO (BF:.96-1.1) | Electronic | 1 | 48 | 3 | 32 | 98 | F43LL-H
F43LL-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (3) 48", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 1 | 48 | 3 | 32 | 76 | F43LL-R
F43RSILL | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (3) 48", 25W T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 48 | 3 | 25 | 65 | F43RSILL
F43RSILL-H | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (3) 48", 25W T-8 lamp, Instant Start Ballast, HLO (BF:.96 - 1.2) | Electronic | 1 | 48 | 3 | 25 | 87 | F43RSILL-H
F43RSILL-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (3) 48", 25W T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 1 | 48 | 3 | 25 | 57 | F43RSILL-R
F43SE | Linear Fluorescent | T12 Linear Fluorescent | F40T12 | Fluorescent, (3) 48", STD lamp | Mag-ES | 1 | 48 | 3 | 40 | 136 | F43ILL
F43SHS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/HO | Fluorescent, (3) 48", STD HO lamp | Mag-STD | 1 | 48 | 3 | 60 | 230 | F43ILL
F43SIL | Linear Fluorescent | T12 Linear Fluorescent | F40T12 | Fluorescent, (3) 48", STD IS lamp, Electronic ballast | Electronic | 1 | 48 | 3 | 39 | 120 | F43ILL
F43SILL | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (3) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 48 | 3 | 30 | 78 | F43SILL
F43SILL-H | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (3) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-3.3) | Electronic | 1 | 48 | 3 | 30 | 105 | F43SILL-H
F43SILL-R | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (3) 48", Super T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 1 | 48 | 3 | 30 | 70 | F43SILL-R
F43SIS | Linear Fluorescent | T12 Linear Fluorescent | F48T12 | Fluorescent, (3) 48", STD IS lamp | Mag-STD | 1 | 48 | 3 | 39 | 162 | F43ILL
F43SS | Linear Fluorescent | T12 Linear Fluorescent | F40T12 | Fluorescent, (3) 48", STD lamp | Mag-STD | 1 | 48 | 3 | 40 | 151 | F43ILL
F43SSILL | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (3) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 48 | 3 | 28 | 72 | F43SSILL
F43SSILL-H | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (3) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-3.3) | Electronic | 1 | 48 | 3 | 28 | 98 | F43SSILL-H
F43SSILL-R | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (3) 48", Super T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 1 | 48 | 3 | 28 | 66 | F43SSILL-R
F43SVS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/VHO | Fluorescent, (3) 48", STD VHO lamp | Mag-STD | 1 | 48 | 3 | 110 | 377 | F43ILL
F44EE | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (4) 48", ES lamp | Mag-ES | 1 | 48 | 4 | 34 | 144 | F44ILL
F44EE/D4 | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (4) 48", ES lamp, 4 Ballasts (delamped) | Mag-ES | 1 | 48 | 4 | 34 | 152 | F44ILL
F44EHS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/HO/ES | Fluorescent, (4) 48", ES HO lamp | Mag-STD | 1 | 48 | 4 | 55 | 270 | F44ILL
F44EIS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/ES | Fluorescent, (4) 48" ES Instant Start lamp, Magnetic ballast | Mag-STD | 1 | 48 | 4 | 30 | 164 | F44ILL
F44EL | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (4) 48", T12 ES lamp, Electronic Ballast | Electronic | 1 | 48 | 4 | 34 | 120 | F44ILL
F44ES | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (4) 48", ES lamp | Mag-STD | 1 | 48 | 4 | 34 | 160 | F44ILL
F44EVS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/VHO/ES | Fluorescent, (4) 48", VHO ES lamp | Mag-STD | 1 | 48 | 4 |  | 420 | F44ILL
F44GHL | Linear Fluorescent | T5 Linear Fluorescent | F48T5/HO | Fluorescent, (4) 48", STD HO T5 lamp | Electronic | 1 | 48 | 4 | 54 | 234 | F44GHL
F44GHL-H | Linear Fluorescent | T5 Linear Fluorescent | F54T5/HO | Fluorescent, (4) 48", STD HO T5 lamp HLO (BF: .96-1.2) | Electronic | 1 | 48 | 4 | 54 | 240 | F44GHL-H
F44IAL-R | Linear Fluorescent | T12 Linear Fluorescent | F25T12 | Fluorescent, (4) 48", F25T12 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 1 | 48 | 4 | 25 | 80 | F44ILL
F44ILL | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (4) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 48 | 4 | 32 | 112 | F44ILL
F44ILL/2 | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (4) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), (2) ballast | Electronic | 2 | 48 | 4 | 32 | 118 | F44ILL/2
F44ILL-H | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (4) 48", T-8 lamp, Instant Start Ballast, HLO (BF: .96-1.2) | Electronic | 1 | 48 | 4 | 32 | 144 | F44ILL-H
F44ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (4) 48", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 1 | 48 | 4 | 32 | 102 | F44ILL-R
F44ILL-V | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (4) 48", T-8 lamp, Instant Start Ballast, VHLO (BF>1.1) | Electronic | 1 | 48 | 4 | 32 | 151 | F44ILL-V
F44LE | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (4) 48", T-8 lamp | Mag-ES | 1 | 48 | 4 | 32 | 142 | F44LE
F44LL | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (4) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 48 | 4 | 32 | 118 | F44LL
F44LL/2 | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (4) 48", T-8 lamp, Rapid Start Ballast, NLO (BF: .85-.95), (2) ballast | Electronic | 2 | 48 | 4 | 32 | 120 | F44LL/2
F44LL-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (4) 48", T-8 lamp, Rapid Start Ballast, RLO (BF<0.85) | Electronic | 1 | 48 | 4 | 32 | 105 | F44LL-R
F44RSILL | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (4) 48", 25W T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 48 | 4 | 25 | 85 | F44RSILL
F44RSILL-H | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (4) 48", 25W T-8 lamp, Instant Start Ballast, HLO (BF:.96 - 1.2) | Electronic | 1 | 48 | 4 | 25 | 112 | F44RSILL-H
F44RSILL-R | Linear Fluorescent | T8 Linear Fluorescent | F25T8 | Fluorescent, (4) 48", 25W T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 1 | 48 | 4 | 25 | 76 | F44RSILL-R
F44SE | Linear Fluorescent | T12 Linear Fluorescent | F40T12 | Fluorescent, (4) 48", STD lamp | Mag-ES | 1 | 48 | 4 | 40 | 172 | F44ILL
F44SHS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/HO | Fluorescent, (4) 48", STD HO lamp | Mag-STD | 1 | 48 | 4 | 60 | 290 | F44ILL
F44SIL | Linear Fluorescent | T12 Linear Fluorescent | F48T12 | Fluorescent, (4) 48", STD IS lamp, Electronic ballast | Electronic | 1 | 48 | 4 | 39 | 148 | F44ILL
F44SILL | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (4) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 48 | 4 | 30 | 105 | F44SILL
F44SILL-H | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (4) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-4.4) | Electronic | 1 | 48 | 4 | 30 | 140 | F44SILL-H
F44SILL-R | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (4) 48", Super T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 1 | 48 | 4 | 30 | 91 | F44SILL-R
F44SIS | Linear Fluorescent | T12 Linear Fluorescent | F48T12 | Fluorescent, (4) 48", STD IS lamp | Mag-STD | 1 | 48 | 4 | 39 | 204 | F44ILL
F44SS | Linear Fluorescent | T12 Linear Fluorescent | F40T12 | Fluorescent, (4) 48", STD lamp | Mag-STD | 1 | 48 | 4 | 40 | 188 | F44ILL
F44SSILL | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (4) 48", Super T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 48 | 4 | 28 | 96 | F44SSILL
F44SSILL-H | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (4) 48", Super T-8 lamp, Instant Start Ballast, HLO (BF:.96-4.4) | Electronic | 1 | 48 | 4 | 28 | 131 | F44SSILL-H
F44SSILL-R | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (4) 48", Super T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 1 | 48 | 4 | 28 | 86 | F44SSILL-R
F44SVS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/VHO | Fluorescent, (4) 48", STD VHO lamp | Mag-STD | 1 | 48 | 4 | 110 | 484 | F44ILL
F45GHL | Linear Fluorescent | T5 Linear Fluorescent | F48T5/HO | Fluorescent, (5) 48", STD HO T5 lamp | Electronic | 1 | 48 | 5 | 54 | 294 | F45GHL
F45ILL | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (5) 48", T-8 lamp, (1) 3-lamp IS ballast and (1) 2-lamp IS ballast, NLO (BF: .85-.95) | Electronic | 1 | 48 | 5 | 32 | 148 | F45ILL
F46EE | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (6) 48", ES lamp | Mag-ES | 1 | 48 | 6 | 34 | 216 | F46ILL
F46EHS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/HO/ES | Fluorescent, (6) 48", ES HO lamp (3.5' lamp) | Mag-STD | 1 | 48 | 6 | 55 | 405 | F46ILL
F46EL | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (6) 48", ES lamp | Electronic | 1 | 48 | 6 | 34 | 186 | F46ILL
F46ES | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (6) 48", ES lamp | Mag-STD | 1 | 48 | 6 | 34 | 236 | F46ILL
F46GHL | Linear Fluorescent | T5 Linear Fluorescent | F48T5/HO | Fluorescent, (6) 48", STD HO T5 lamp | Electronic | 1 | 48 | 6 | 54 | 351 | F46GHL
F46GHL-H | Linear Fluorescent | T5 Linear Fluorescent | F54T5/HO | Fluorescent, (6) 48", STD HO T5 lamp HLO (BF: .96-1.2) | Electronic | 1 | 48 | 6 | 54 | 364 | F46GHL-H
F46ILL | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (6) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 48 | 6 | 32 | 175 | F46ILL
F46ILL-H | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (6) 48", T-8 lamp, Instant Start Ballast, HLO (BF: .96-1.2) | Electronic | 1 | 48 | 6 | 32 | 222 | F46ILL-H
F46ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (6) 48", T-8 lamp, Instant Start Ballast, RLO (BF< .85) | Electronic | 1 | 48 | 6 | 32 | 156 | F46ILL-R
F46ILL-V | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (6) 48", T-8 lamp, Instant Start Ballast, VLO (BF: >1.2) | Electronic | 1 | 48 | 6 | 32 | 255 | F46ILL-V
F46LL | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (6) 48", T-8 lamp, NLO (BF: .85-.95) | Electronic | 1 | 48 | 6 | 32 | 182 | F46LL
F46SE | Linear Fluorescent | T12 Linear Fluorescent | F40T12 | Fluorescent, (6) 48", STD lamp | Mag-ES | 1 | 48 | 6 | 40 | 258 | F46ILL
F46SIL | Linear Fluorescent | T8 Linear Fluorescent | F30T8 | Fluorescent, (6) 48", 30W T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 48 | 6 | 32 | 158 | F46SIL
F46SS | Linear Fluorescent | T12 Linear Fluorescent | F40T12 | Fluorescent, (6) 48", STD lamp | Mag-STD | 1 | 48 | 6 | 40 | 282 | F46ILL
F46SSIL | Linear Fluorescent | T8 Linear Fluorescent | F28T8 | Fluorescent, (6) 48", 28W T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 48 | 6 | 32 | 144 | F46SSIL
F48EE | Linear Fluorescent | T12 Linear Fluorescent | F40T12/ES | Fluorescent, (8) 48", ES lamp | Mag-ES | 1 | 48 | 8 | 34 | 288 | F48ILL
F48EHS | Linear Fluorescent | T12 Linear Fluorescent | F48T12/HO/ES | Fluorescent, (8) 48", ES HO lamp (3.5' lamp) | Mag-STD | 1 | 48 | 8 | 55 | 540 | F48ILL
F48GHL | Linear Fluorescent | T5 Linear Fluorescent | F48T5/HO | Fluorescent, (8) 48", STD HO T5 lamp | Electronic | 1 | 48 | 8 | 54 | 468 | F48GHL
F48ILL | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (8) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 48 | 8 | 32 | 224 | F48ILL
F48ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F32T8 | Fluorescent, (8) 48", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 1 | 48 | 8 | 32 | 204 | F48ILL-R
F48LHL | Linear Fluorescent | T8 Linear Fluorescent | F48T8/HO | Fluorescent, (8) 48", T-8 HO lamp, NLO (BF: 0.95), 4 Ballasts | Electronic | 1 | 48 | 8 | 44 | 392 | F48LHL
F51GHL | Linear Fluorescent | T5 Linear Fluorescent | F60T5/HO | Fluorescent, (1) 60", STD HO T5 lamp | Electronic | 1 | 60 | 1 | 80 | 89 | F51GHL
F51GL | Linear Fluorescent | T5 Linear Fluorescent | F60T5 | Fluorescent, (1) 60", STD T5 lamp | Electronic | 1 | 60 | 1 | 35 | 39 | F51GL
F51ILHL | Linear Fluorescent | T8 Linear Fluorescent | F60T8/HO | Fluorescent, (1) 60", T-8 HO lamp, Instant Start Ballast | Electronic | 1 | 60 | 1 | 55 | 59 | N/A
F51ILL | Linear Fluorescent | T8 Linear Fluorescent | F40T8 | Fluorescent, (1) 60", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 60 | 1 | 40 | 36 | F51ILL
F51ILL/T2 | Linear Fluorescent | T8 Linear Fluorescent | F40T8 | Fluorescent, (1) 60", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 60 | 1 | 40 | 36 | F51ILL/T2
F51ILL/T3 | Linear Fluorescent | T8 Linear Fluorescent | F40T8 | Fluorescent, (1) 60", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 3 Lamp Ballast | Electronic | 1 | 60 | 1 | 40 | 35 | F51ILL/T3
F51ILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F40T8 | Fluorescent, (1) 60", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 4 Lamp Ballast | Electronic | 1 | 60 | 1 | 40 | 34 | F51ILL/T4
F51ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F40T8 | Fluorescent, (1) 60", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 1 | 60 | 1 | 40 | 43 | F51ILL-R
F51SHE | Linear Fluorescent | T12 Linear Fluorescent | F60T12/HO | Fluorescent, (1) 60", STD HO lamp | Mag-ES | 1 | 60 | 1 | 75 | 88 | F51ILL
F51SHL | Linear Fluorescent | T12 Linear Fluorescent | F60T12/HO | Fluorescent, (1) 60", STD HO lamp | Electronic | 1 | 60 | 1 | 75 | 69 | F51ILL
F51SHS | Linear Fluorescent | T12 Linear Fluorescent | F60T12/HO | Fluorescent, (1) 60", STD HO lamp | Mag-STD | 1 | 60 | 1 | 75 | 92 | F51ILL
F51SL | Linear Fluorescent | T12 Linear Fluorescent | F60T12 | Fluorescent, (1) 60", STD lamp | Electronic | 1 | 60 | 1 | 50 | 44 | F51ILL
F51SS | Linear Fluorescent | T12 Linear Fluorescent | F60T12 | Fluorescent, (1) 60", STD lamp | Mag-STD | 1 | 60 | 1 | 50 | 63 | F51ILL
F51SVS | Linear Fluorescent | T12 Linear Fluorescent | F60T12/VHO | Fluorescent, (1) 60", VHO ES lamp | Mag-STD | 1 | 60 | 1 | 135 | 165 | F51ILL
F52GL | Linear Fluorescent | T5 Linear Fluorescent | F60T5 | Fluorescent, (2) 60", STD T5 lamp | Electronic | 1 | 60 | 2 | 35 | 76 | F52GL
F52ILHL | Linear Fluorescent | T8 Linear Fluorescent | F60T8/HO | Fluorescent, (2) 60", T-8 HO lamp, Instant Start Ballast | Electronic | 1 | 60 | 2 | 55 | 123 | F51ILHL
F52ILL | Linear Fluorescent | T8 Linear Fluorescent | F40T8 | Fluorescent, (2) 60", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 60 | 2 | 40 | 72 | F52ILL
F52ILL/T4 | Linear Fluorescent | T8 Linear Fluorescent | F40T8 | Fluorescent, (2) 60", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 60 | 2 | 40 | 67 | F52ILL/T4
F52ILL-H | Linear Fluorescent | T8 Linear Fluorescent | F40T8 | Fluorescent, (2) 60", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 1 | 60 | 2 | 40 | 80 | F52ILL-H
F52ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F40T8 | Fluorescent, (2) 60", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 1 | 60 | 2 | 40 | 73 | F52ILL-R
F52SHE | Linear Fluorescent | T12 Linear Fluorescent | F60T12/HO | Fluorescent, (2) 60", STD HO lamp | Mag-ES | 1 | 60 | 2 | 75 | 176 | F52ILL
F52SHL | Linear Fluorescent | T12 Linear Fluorescent | F60T12/HO | Fluorescent, (2) 60", STD HO lamp | Electronic | 1 | 60 | 2 | 75 | 138 | F52ILL
F52SHS | Linear Fluorescent | T12 Linear Fluorescent | F60T12/HO | Fluorescent, (2) 60", STD HO lamp | Mag-STD | 1 | 60 | 2 | 75 | 168 | F52ILL
F52SL | Linear Fluorescent | T12 Linear Fluorescent | F60T12 | Fluorescent, (2) 60", STD lamp | Electronic | 1 | 60 | 2 | 50 | 88 | F52ILL
F52SS | Linear Fluorescent | T12 Linear Fluorescent | F60T12 | Fluorescent, (2) 60", STD lamp | Mag-STD | 1 | 60 | 2 | 50 | 128 | F52ILL
F52SVS | Linear Fluorescent | T12 Linear Fluorescent | F60T12/VHO | Fluorescent, (2) 60", VHO ES lamp | Mag-STD | 1 | 60 | 2 | 135 | 310 | F52ILL
F53ILL | Linear Fluorescent | T8 Linear Fluorescent | F40T8 | Fluorescent, (3) 60", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 60 | 3 | 40 | 106 | F53ILL
F53ILL-H | Linear Fluorescent | T8 Linear Fluorescent | F40T8 | Fluorescent, (3) 60", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 1 | 60 | 3 | 40 | 108 | F53ILL-H
F54ILL | Linear Fluorescent | T8 Linear Fluorescent | F40T8 | Fluorescent, (4) 60", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 60 | 4 | 40 | 134 | F54ILL
F54ILL-H | Linear Fluorescent | T8 Linear Fluorescent | F40T8 | Fluorescent, (4) 60", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 1 | 60 | 4 | 40 | 126 | F54ILL-H
F61ISL | Linear Fluorescent | T12 Linear Fluorescent | F72T12 | Fluorescent, (1) 72", STD lamp, IS electronic ballast | Electronic | 1 | 72 | 1 | 55 | 68 | F61ILL
F61SE | Linear Fluorescent | T12 Linear Fluorescent | F72T12 | Fluorescent, (1) 72", STD lamp | Mag-ES | 1 | 72 | 1 | 55 | 76 | F61ILL
F61SHS | Linear Fluorescent | T12 Linear Fluorescent | F72T12/HO | Fluorescent, (1) 72", STD HO lamp | Mag-STD | 1 | 72 | 1 | 85 | 120 | F61ILL
F61SS | Linear Fluorescent | T12 Linear Fluorescent | F72T12 | Fluorescent, (1) 72", STD lamp | Mag-STD | 1 | 72 | 1 | 55 | 90 | F61ILL
F61SVS | Linear Fluorescent | T12 Linear Fluorescent | F72T12/VHO | Fluorescent, (1) 72", VHO lamp | Mag-STD | 1 | 72 | 1 | 160 | 180 | F61ILL
F62ILHL | Linear Fluorescent | T8 Linear Fluorescent | F72T8 | Fluorescent, (2) 72", T-8 HO lamp, Instant Start Ballast | Electronic | 1 | 72 | 2 | 65 | 147 | F62ILHL
F62ISL | Linear Fluorescent | T12 Linear Fluorescent | F72T12 | Fluorescent, (2) 72", STD lamp, IS electronic ballast | Electronic | 1 | 72 | 2 | 55 | 108 | F62ILL
F62SE | Linear Fluorescent | T12 Linear Fluorescent | F72T12 | Fluorescent, (2) 72", STD lamp | Mag-ES | 1 | 72 | 2 | 55 | 122 | F62ILL
F62SHE | Linear Fluorescent | T12 Linear Fluorescent | F72T12/HO | Fluorescent, (2) 72", STD HO lamp | Mag-ES | 1 | 72 | 2 | 85 | 194 | F62ILL
F62SHS | Linear Fluorescent | T12 Linear Fluorescent | F72T12/HO | Fluorescent, (2) 72", STD HO lamp | Mag-STD | 1 | 72 | 2 | 85 | 220 | F62ILL
F62SL | Linear Fluorescent | T12 Linear Fluorescent | F72T12 | Fluorescent, (2) 72", STD lamp | Electronic | 1 | 72 | 2 | 55 | 108 | F62ILL
F62SS | Linear Fluorescent | T12 Linear Fluorescent | F72T12 | Fluorescent, (2) 72", STD lamp | Mag-STD | 1 | 72 | 2 | 55 | 145 | F62ILL
F62SVS | Linear Fluorescent | T12 Linear Fluorescent | F72T12/VHO | Fluorescent, (2) 72", VHO lamp | Mag-STD | 1 | 72 | 2 | 160 | 330 | F62ILL
F63ISL | Linear Fluorescent | T12 Linear Fluorescent | F72T12 | Fluorescent, (3) 72", STD lamp, IS electronic ballast | Electronic | 1 | 72 | 3 | 55 | 176 | F63ILL
F63SS | Linear Fluorescent | T12 Linear Fluorescent | F72T12 | Fluorescent, (3) 72", STD lamp | Mag-STD | 1 | 72 | 3 | 55 | 202 | F63ILL
F64ISL | Linear Fluorescent | T12 Linear Fluorescent | F72T12 | Fluorescent, (4) 72", STD lamp, IS electronic ballast | Electronic | 1 | 72 | 4 | 55 | 216 | F64ILL
F64SE | Linear Fluorescent | T12 Linear Fluorescent | F72T12 | Fluorescent, (4) 72", STD lamp | Mag-ES | 1 | 72 | 4 | 55 | 230 | F64ILL
F64SHE | Linear Fluorescent | T12 Linear Fluorescent | F72T12/HO | Fluorescent, (4) 72", STD HO lamp | Mag-ES | 1 | 72 | 4 | 85 | 388 | F64ILL
F64SS | Linear Fluorescent | T12 Linear Fluorescent | F72T12 | Fluorescent, (4) 72", STD lamp | Mag-STD | 1 | 72 | 4 | 55 | 244 | F64ILL
F81EE | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (1) 96", ES lamp | Mag-ES | 1 | 96 | 1 | 60 | 61 | F81ILL
F81EE/T2 | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (1) 96", ES lamp, tandem to 2-lamp ballast | Mag-ES | 1 | 96 | 1 | 60 | 62 | F81ILL
F81EHL | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO/ES | Fluorescent, (1) 96", ES HO lamp | Electronic | 1 | 96 | 1 | 95 | 80 | F81LHL
F81EHL/T2 | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO/ES | Fluorescent, (1) 96", ES HO lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 96 | 1 | 95 | 85 | F81LHL
F81EHS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO/ES | Fluorescent, (1) 96", ES HO lamp | Mag-STD | 1 | 96 | 1 | 95 | 125 | F81LHL
F81EL | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (1) 96", ES lamp | Electronic | 1 | 96 | 1 | 60 | 60 | F81ILL
F81EL/T2 | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (1) 96", ES lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 96 | 1 | 60 | 55 | F81ILL
F81ES | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (1) 96", ES lamp | Mag-STD | 1 | 96 | 1 | 60 | 83 | F81ILL
F81ES/T2 | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (1) 96", ES lamp, tandem to 2-lamp ballast | Mag-STD | 1 | 96 | 1 | 60 | 64 | F81ILL
F81EVS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/VHO/ES | Fluorescent, (1) 96", ES VHO lamp | Mag-STD | 1 | 96 | 1 | 185 | 200 | F81LHL
F81ILL | Linear Fluorescent | T8 Linear Fluorescent | F96T8 | Fluorescent, (1) 96", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 96 | 1 | 59 | 58 | F81ILL
F81ILL/T2 | Linear Fluorescent | T8 Linear Fluorescent | F96T8 | Fluorescent, (1) 96", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 96 | 1 | 59 | 55 | F81ILL/T2
F81ILL/T2-R | Linear Fluorescent | T8 Linear Fluorescent | F96T8 | Fluorescent, (1) 96", T-8 lamp, Instant Start Ballast, RLO (BF<.85), Tandem 2 Lamp Ballast | Electronic | 1 | 96 | 1 | 59 | 49 | F81ILL/T2-R
F81ILL-H | Linear Fluorescent | T8 Linear Fluorescent | F96T8 | Fluorescent, (1) 96", T-8 lamp, Instant Start Ballast, HLO (BF:.96-1.1) | Electronic | 1 | 96 | 1 | 59 | 68 | F81ILL-H
F81ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F96T8 | Fluorescent, (1) 96", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 1 | 96 | 1 | 59 | 57 | F81ILL-R
F81ILL-V | Linear Fluorescent | T8 Linear Fluorescent | F96T8 | Fluorescent, (1) 96", T-8 lamp, Instant Start Ballast, VHLO (BF>1.1) | Electronic | 1 | 96 | 1 | 59 | 71 | F81ILL-V
F81LHL | Linear Fluorescent | T8 Linear Fluorescent | F96T8/HO | Fluorescent, (1) 96", T8 HO lamp | Electronic | 1 | 96 | 1 | 86 | 85 | F81LHL
F81LHL/T2 | Linear Fluorescent | T8 Linear Fluorescent | F96T8/HO | Fluorescent, (1) 96", T8 HO lamp, tandem wired to 2-lamp ballast | Electronic | 1 | 96 | 1 | 86 | 80 | F81LHL/T2
F81SE | Linear Fluorescent | T12 Linear Fluorescent | F96T12 | Fluorescent, (1) 96", STD lamp | Mag-ES | 1 | 96 | 1 | 75 | 91 | F81ILL
F81SHE | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO | Fluorescent, (1) 96", STD HO lamp | Mag-ES | 1 | 96 | 1 | 110 | 132 | F81LHL
F81SHL/T2 | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO | Fluorescent, (1) 96", STD HO lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 96 | 1 | 110 | 98 | F81LHL
F81SHS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO | Fluorescent, (1) 96", STD HO lamp | Mag-STD | 1 | 96 | 1 | 110 | 145 | F81LHL
F81SL | Linear Fluorescent | T12 Linear Fluorescent | F96T12 | Fluorescent, (1) 96", STD lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 96 | 1 | 75 | 70 | F81ILL
F81SL/T2 | Linear Fluorescent | T12 Linear Fluorescent | F96T12 | Fluorescent, (1) 96", STD lamp, Rapid Start Ballast, NLO (BF: .85-.95), Tandem 2 Lamp Ballast | Electronic | 1 | 96 | 1 | 75 | 67 | F81ILL
F81SS | Linear Fluorescent | T12 Linear Fluorescent | F96T12 | Fluorescent, (1) 96", STD lamp | Mag-STD | 1 | 96 | 1 | 75 | 100 | F81ILL
F81SVS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/VHO | Fluorescent, (1) 96", STD VHO lamp | Mag-STD | 1 | 96 | 1 | 215 | 230 | F81LHL
F82EE | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (2) 96", ES lamp | Mag-ES | 1 | 96 | 2 | 60 | 123 | F82ILL
F82EHE | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO/ES | Fluorescent, (2) 96", ES HO lamp | Mag-ES | 1 | 96 | 2 | 95 | 207 | F82LHL
F82EHL | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO/ES | Fluorescent, (2) 96", ES HO lamp | Electronic | 1 | 96 | 2 | 95 | 170 | F82LHL
F82EHS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO/ES | Fluorescent, (2) 96", ES HO lamp | Mag-STD | 1 | 96 | 2 | 95 | 227 | F82LHL
F82EL | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (2) 96", ES lamp | Electronic | 1 | 96 | 2 | 60 | 110 | F82ILL
F82ES | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (2) 96", ES lamp | Mag-STD | 1 | 96 | 2 | 60 | 138 | F82ILL
F82EVS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/VHO/ES | Fluorescent, (2) 96", ES VHO lamp | Mag-STD | 1 | 96 | 2 | 185 | 390 | F82LHL
F82ILL | Linear Fluorescent | T8 Linear Fluorescent | F96T8 | Fluorescent, (2) 96", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 96 | 2 | 59 | 109 | F82ILL
F82ILL-R | Linear Fluorescent | T8 Linear Fluorescent | F96T8 | Fluorescent, (2) 96", T-8 lamp, Instant Start Ballast, RLO (BF<0.85) | Electronic | 1 | 96 | 2 | 59 | 98 | F82ILL-R
F82LHL | Linear Fluorescent | T8 Linear Fluorescent | F96T8/HO | Fluorescent, (2) 96", T8 HO lamp | Electronic | 1 | 96 | 2 | 86 | 160 | F82LHL
F82SE | Linear Fluorescent | T12 Linear Fluorescent | F96T12 | Fluorescent, (2) 96", STD lamp | Mag-ES | 1 | 96 | 2 | 75 | 158 | F82ILL
F82SHE | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO | Fluorescent, (2) 96", STD HO lamp | Mag-ES | 1 | 96 | 2 | 110 | 237 | F82LHL
F82SHL | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO | Fluorescent, (2) 96", STD HO lamp | Electronic | 1 | 96 | 2 | 110 | 195 | F82LHL
F82SHS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO | Fluorescent, (2) 96", STD HO lamp | Mag-STD | 1 | 96 | 2 | 110 | 257 | F82LHL
F82SL | Linear Fluorescent | T12 Linear Fluorescent | F96T12 | Fluorescent, (2) 96", STD lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 96 | 2 | 75 | 134 | F82ILL
F82SS | Linear Fluorescent | T12 Linear Fluorescent | F96T12 | Fluorescent, (2) 96", STD lamp | Mag-STD | 1 | 96 | 2 | 75 | 173 | F82ILL
F82SVS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/VHO | Fluorescent, (2) 96", STD VHO lamp | Mag-STD | 1 | 96 | 2 | 215 | 450 | F82LHL
F83EE | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (3) 96", ES lamp | Mag-ES | 1 | 96 | 3 | 60 | 210 | F83ILL
F83EHE | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO/ES | Fluorescent, (3) 96", ES HO lamp, (1) 2-lamp ES Ballast, (1) 1-lamp STD Ballast | Mag-ES/STD | 1 | 96 | 3 | 95 | 319 | F83LHL
F83EHS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO/ES | Fluorescent, (3) 96", ES HO lamp | Mag-STD | 1 | 96 | 3 | 95 | 352 | F83LHL
F83EL | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (3) 96", ES lamp | Electronic | 1 | 96 | 3 | 60 | 179 | F83ILL
F83ES | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (3) 96", ES lamp | Mag-STD | 1 | 96 | 3 | 60 | 221 | F83ILL
F83EVS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/VHO/ES | Fluorescent, (3) 96", ES VHO lamp | Mag-STD | 1 | 96 | 3 | 185 | 590 | F83LHL
F83ILL | Linear Fluorescent | T8 Linear Fluorescent | F96T8 | Fluorescent, (3) 96", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 96 | 3 | 59 | 167 | F83ILL
F83SHS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO | Fluorescent, (3) 96", STD HO lamp | Mag-STD | 1 | 96 | 3 | 110 | 392 | F83LHL
F83SS | Linear Fluorescent | T12 Linear Fluorescent | F96T12 | Fluorescent, (3) 96", STD lamp | Mag-STD | 1 | 96 | 3 | 75 | 273 | F83ILL
F83SVS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/VHO | Fluorescent, (3) 96", STD VHO lamp | Mag-STD | 1 | 96 | 3 | 215 | 680 | F83LHL
F84EE | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (4) 96", ES lamp | Mag-ES | 1 | 96 | 4 | 60 | 246 | F84ILL
F84EHE | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO/ES | Fluorescent, (4) 96", ES HO lamp | Mag-ES | 1 | 96 | 4 | 95 | 414 | F84LHL
F84EHL | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO/ES | Fluorescent, (4) 96", ES HO lamp | Electronic | 1 | 96 | 4 | 95 | 340 | F84LHL
F84EHS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO/ES | Fluorescent, (4) 96", ES HO lamp | Mag-STD | 1 | 96 | 4 | 95 | 454 | F84LHL
F84EL | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (4) 96", ES lamp | Electronic | 1 | 96 | 4 | 60 | 220 | F84ILL
F84ES | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (4) 96", ES lamp | Mag-STD | 1 | 96 | 4 | 60 | 276 | F84ILL
F84EVS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/VHO/ES | Fluorescent, (4) 96", ES VHO lamp | Mag-STD | 1 | 96 | 4 | 185 | 780 | F84LHL
F84ILL | Linear Fluorescent | T8 Linear Fluorescent | F96T8 | Fluorescent, (4) 96", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 96 | 4 | 59 | 219 | F84ILL
F84LHL | Linear Fluorescent | T8 Linear Fluorescent | F96T8/HO | Fluorescent, (4) 96", T8 HO lamp | Electronic | 1 | 96 | 4 | 86 | 320 | F84LHL
F84SE | Linear Fluorescent | T12 Linear Fluorescent | F96T12 | Fluorescent, (4) 96", STD lamp | Mag-ES | 1 | 96 | 4 | 75 | 316 | F84ILL
F84SHE | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO | Fluorescent, (4) 96", STD HO lamp | Mag-ES | 1 | 96 | 4 | 110 | 474 | F84LHL
F84SHL | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO | Fluorescent, (4) 96", STD HO lamp | Electronic | 1 | 96 | 4 | 110 | 390 | F84LHL
F84SHS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO | Fluorescent, (4) 96", STD HO lamp | Mag-STD | 1 | 96 | 4 | 110 | 514 | F84LHL
F84SL | Linear Fluorescent | T12 Linear Fluorescent | F96T12 | Fluorescent, (4) 96", STD lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 96 | 4 | 75 | 268 | F84ILL
F84SS | Linear Fluorescent | T12 Linear Fluorescent | F96T12 | Fluorescent, (4) 96", STD lamp | Mag-STD | 1 | 96 | 4 | 75 | 346 | F84ILL
F84SVS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/VHO | Fluorescent, (4) 96", STD VHO lamp | Mag-STD | 1 | 96 | 4 | 215 | 900 | F84LHL
F86EE | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (6) 96", ES lamp | Mag-ES | 1 | 96 | 6 | 60 | 369 | F86ILL
F86EHS | Linear Fluorescent | T12 Linear Fluorescent | F96T12/HO/ES | Fluorescent, (6) 96", ES HO lamp | Mag-STD | 1 | 96 | 6 | 95 | 721 | F86LHL
F86EL | Linear Fluorescent | T12 Linear Fluorescent | F96T12/ES | Fluorescent, (6) 96", ES lamp | Electronic | 1 | 96 | 6 | 60 | 330 | F86ILL
F86ILL | Linear Fluorescent | T8 Linear Fluorescent | F96T8 | Fluorescent, (6) 96", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | Electronic | 1 | 96 | 6 | 59 | 328 | F86ILL
F26ILL | T12 EPACT/EISA Baseline | EPACT/EISA Compliance | N/A | Baseline Code for 24" 6-Lamp T12 EPACT/EISA Compliant T8 | N/A | 1 | 24 | 6 | 17 | 87 | N/A
F36ILL | T12 EPACT/EISA Baseline | EPACT/EISA Compliance | N/A | Baseline Code for 36" 6-Lamp T12 EPACT/EISA Compliant T8 | N/A | 1 | 36 | 6 | 25 | 128 | N/A
F61ILL | T12 EPACT/EISA Baseline | EPACT/EISA Compliance | N/A | Baseline Code for 72" 1-Lamp T12 EPACT/EISA Compliant T8 | N/A | 1 | 72 | 1 | 65 | 55 | N/A
F62ILL | T12 EPACT/EISA Baseline | EPACT/EISA Compliance | N/A | Baseline Code for 72" 2-Lamp T12 EPACT/EISA Compliant T8 | N/A | 1 | 72 | 2 | 65 | 111 | N/A
F63ILL | T12 EPACT/EISA Baseline | EPACT/EISA Compliance | N/A | Baseline Code for 72" 3-Lamp T12 EPACT/EISA Compliant T8 | N/A | 1 | 72 | 3 | 65 | 166 | N/A
F64ILL | T12 EPACT/EISA Baseline | EPACT/EISA Compliance | N/A | Baseline Code for 72" 4-Lamp T12 EPACT/EISA Compliant T8 | N/A | 1 | 72 | 4 | 65 | 221 | N/A
F83LHL | T12 EPACT/EISA Baseline | EPACT/EISA Compliance | N/A | Baseline Code for 96" 3-Lamp T12HO EPACT/EISA Compliant T8 | N/A | 1 | 96 | 3 | 86 | 253 | N/A
F86LHL | T12 EPACT/EISA Baseline | EPACT/EISA Compliance | N/A | Baseline Code for 96" 6-Lamp T12HO EPACT/EISA Compliant T8 | N/A | 1 | 96 | 6 | 86 | 506 | N/A
FU1EE | U-Tube Fluorescent | U-Tube Fluorescent | FU40T12/ES | Fluorescent, (1) U-Tube, ES lamp | Mag-ES | 1 | 24 | 1 | 34 | 43 | FU1ILL
FU1ILL | U-Tube Fluorescent | U-Tube Fluorescent | FU31T8/6 | Fluorescent, (1) U-Tube, T-8 lamp, Instant Start ballast | Electronic | 1 | 24 | 1 | 32 | 31 | FU1ILL
FU1LL | U-Tube Fluorescent | U-Tube Fluorescent | FU31T8/6 | Fluorescent, (1) U-Tube, T-8 lamp | Electronic | 1 | 24 | 1 | 32 | 32 | FU1LL
FU1LL-R | U-Tube Fluorescent | U-Tube Fluorescent | FU31T8/6 | Fluorescent, (1) U-Tube, T-8 lamp, RLO (BF<0.85) | Electronic | 1 | 24 | 1 | 31 | 27 | FU1LL-R
FU2EE | U-Tube Fluorescent | U-Tube Fluorescent | FU40T12/ES | Fluorescent, (2) U-Tube, ES lamp | Mag-ES | 1 | 24 | 2 | 34 | 72 | FU2ILL
FU2ES | U-Tube Fluorescent | U-Tube Fluorescent | FU40T12/ES | Fluorescent, (2) U-Tube, ES lamp | Mag-STD | 1 | 24 | 2 | 34 | 82 | FU2ILL
FU2ILL | U-Tube Fluorescent | U-Tube Fluorescent | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamp, Instant Start Ballast | Electronic | 1 | 24 | 2 | 32 | 59 | FU2ILL
FU2ILL/T4 | U-Tube Fluorescent | U-Tube Fluorescent | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamp, Instant Start Ballast, tandem wired | Electronic | 1 | 24 | 2 | 32 | 56 | FU2ILL/T4
FU2ILL/T4-R | U-Tube Fluorescent | U-Tube Fluorescent | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamp, Instant Start Ballast, RLO, tandem wired | Electronic | 1 | 24 | 2 | 32 | 51 | FU2ILL/T4-R
FU2ILL-H | U-Tube Fluorescent | U-Tube Fluorescent | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamp, Instant Start HLO Ballast | Electronic | 1 | 24 | 2 | 32 | 65 | FU2ILL-H
FU2ILL-R | U-Tube Fluorescent | U-Tube Fluorescent | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamp, Instant Start RLO Ballast | Electronic | 1 | 24 | 2 | 32 | 52 | FU2ILL-R
FU2LL | U-Tube Fluorescent | U-Tube Fluorescent | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamp | Electronic | 1 | 24 | 2 | 32 | 60 | FU2LL
FU2LL/T2 | U-Tube Fluorescent | U-Tube Fluorescent | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamp, Tandem 4 lamp ballast | Electronic | 1 | 24 | 2 | 32 | 59 | FU2LL/T2
FU2LL-R | U-Tube Fluorescent | U-Tube Fluorescent | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamp, RLO (BF<0.85) | Electronic | 1 | 24 | 2 | 31 | 54 | FU2LL-R
FU2SE | U-Tube Fluorescent | U-Tube Fluorescent | FU40T12 | Fluorescent, (2) U-Tube, STD lamp | Mag-ES | 1 | 24 | 2 | 40 | 85 | FU2ILL
FU2SS | U-Tube Fluorescent | U-Tube Fluorescent | FU40T12 | Fluorescent, (2) U-Tube, STD lamp | Mag-STD | 1 | 24 | 2 | 40 | 96 | FU2ILL
FU3EE | U-Tube Fluorescent | U-Tube Fluorescent | FU40T12/ES | Fluorescent, (3) U-Tube, ES lamp | Mag-ES | 1 | 24 | 3 | 35 | 115 | FU3ILL
FU3ILL | U-Tube Fluorescent | U-Tube Fluorescent | FU31T8/6 | Fluorescent, (3) U-Tube, T-8 lamp, Instant Start Ballast | Electronic | 1 | 24 | 3 | 32 | 89 | FU3ILL
FU3ILL-R | U-Tube Fluorescent | U-Tube Fluorescent | FU31T8/6 | Fluorescent, (3) U-Tube, T-8 lamp, Instant Start RLO Ballast | Electronic | 1 | 24 | 3 | 32 | 78 | FU3ILL-R
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A
Enter Custom Fixture |  | Custom, From Cut Sheet | N/A |  | N/A

## Version Log (hidden)
Version Log
Original Author: |  | Michael Stevenson | QA/QC Engineer(s):
Primary Developer: |  | Michael Stevenson | Senior Engineer Approval:
Version | Date | Reason for Change | Change Description | Contact, Department
1 | 2017-12-29 | Initial Launch |  | Michael Stevenson, Engineering
1.1 | 2018-01-16 | Dropdown Fix | Fixed issue with Measure dropdown | Michael Stevenson, Engineering
1.2 | 2018-01-23 | Filter Fix | Fixed issue with filter on Fixture Codes tab | Michael Stevenson, Engineering
1.3 | 2018-01-24 | Bug & Format | Fixed issue with HVAC type & file format | Michael Stevenson, Engineering
1.4 | 2018-02-08 | Lookup Issue | Fixed issut with HVAC lookup | Michael Stevenson, Engineering
1.5 | 2018-02-23 | Reconfiguration, Lookup table updates, 50% project cost cap | Removed Building Type input from calculator tab Removed requirement to select measure before selecting fixture codes Corrected HVAC lookup Updated Building Type list format Implemented 50% Project Cost cap | Michael Stevenson, Engineering
1.6 | 2018-03-07 | Lookup table updates, bug fixes | Added Measure Name from Filing, pre & post fixture descriptions, measure life mapping, corrected issue with controls incentive calculation | Michael Stevenson, Engineering
1.7 | 2018-03-28 | Measure Life Update | Updated measure lives to match filing. | Michael Stevenson, Engineering
1.8 | 2018-07-12 | Incentive Update & General Edits | Updated incentive for LED mogul-screw base replacement for HID lamps to $68 to match measure list. Updated Savings and Incentive Summary Table to match required DSMT inputs. Inserted input message for equipment costs on calculator tab. | Michael Stevenson, Engineering
1.9 | 2018-12-07 | General Updates | Updated kW PJM savings for controls Created per unit fixture and controls equipment cost input. Updated total fixture and controls equipment cost to calculate accordingly. Deleted Measure Summary tab to save space. Updated description of high bay versus low bay to include ceiling height threshold. | Michael Stevenson, Engineering
2 | 2019-09-10 | Cell Protection Updates | Updated cell protections so that formulas in hidden columns cannot be deleted when an array is selected and delete/backspace is pressed. | Michael Stevenson, Engineering
3 | 2020-03-06 | Lookups & Data Validation | Added lookups for measure and controls codes. Added data validation for text fields to not exceed 55 characters. | Michael Stevenson, Engineering
3.1 | 2020-04-03 | Lookups & Data Validation | Modified control type code and added data validation for custom fixture code descriptions. | Michael Stevenson, Engineering
4 | 2020-12-22 | Phase V Update | Updated incentive rates based on Phase V incentive table. Updated HOU reference for exit sign measures. | Meredith Woy, Engineering
4.1 | 2021-02-17 | Lighting - Other, Lighting - Custom | Updated incentive rate for Lighting - other. Added Lighting - Custom | Meredith Woy, Engineering