## Incentives (hidden)
Ready for QC | Potomac Edison Measure Category / Modeled Program | Potomac Edison Measure Name | Table 23 - Statewide C&I Incentives Table: Category | Table 23 - Statewide C&I Incentives Table: Measure Name / Category | Table 23 - Statewide C&I Incentives Table: Measure Eligibility | Unit Paid | Filing Incentive (Up To) | Evaluation / TRM Ref | Potomac Edision Filing Appendix D Table D-4 Measure Name (Filing) | Potomac Edision Filing Appendix D Table D-4 Energy Efficiency Eligibility / Description | Size Requirements | Efficiency Requirements | Tab name | CR Comments
x | HVAC - CI | Air Conditioning C&I - (<=5.4 Ton & SEER >= 16) | Unitary HVAC Equipment | AIR CONDITIONERS AND HEAT PUMPS | Air Conditioning (AC) only - all sizes | Per Ton | 250 | Mid-Atlantic TRM, V10, Pg. 283 | Air Conditioning C&I - (<=5.4 Ton & SEER >= 16) | Installation of Single Package or Split System central units w/ SEER ratings > or = 16. Includes variable flow (VRF) systems. | ≤5.4 tons | ≥16 SEER | Split & Packaged Air Conditioning
x | HVAC - CI | Air Conditioning C&I - ( >5.4 < 20 Ton, >=12 EER or>=13 IEER) | Unitary HVAC Equipment | AIR CONDITIONERS AND HEAT PUMPS | Air Conditioning (AC) only - all sizes | Per Ton | 250 | Mid-Atlantic TRM, V10, Pg. 283 | Air Conditioning C&I - ( >5.4 < 20 Ton, >=12 EER or>=13 IEER) | Installation of a Single Package or Split System central unit exceeding the baselines in International Energy Conservation Code (IECC 2018) by 5%. Includes variable flow (VRF) systems. | >5.4 to <20 tons | Exceeds IECC 2018 by at least 5% | Split & Packaged Air Conditioning
x | HVAC - CI | Air Conditioning C&I - (>=20 Ton, >=10.2 EER or >=11.4 IEER) | Unitary HVAC Equipment | AIR CONDITIONERS AND HEAT PUMPS | Air Conditioning (AC) only - all sizes | Per Ton | 250 | Mid-Atlantic TRM, V10, Pg. 283 | Air Conditioning C&I - (>=20 Ton, >=10.2 EER or >=11.4 IEER) | Installation of a Single Package or Split System central unit exceeding the baselines in International Energy Conservation Code (IECC 2018) by 5%. Includes variable flow (VRF) systems. | ≥20 tons | Exceeds IECC 2018 by at least 5% | Split & Packaged Air Conditioning
x | HVAC - CI | Heat Pump C&I - (<=5.4 Ton & HSPF >= 9) | Unitary HVAC Equipment | WATER-COOLED AND EVAPORATIVE COOLING AIR CONDITIONERS | <5.4 to <11.25 tons | Per Ton | 250 | Mid-Atlantic TRM, V10, Pg. 283 | Heat Pump C&I - (<=5.4 Ton & HSPF >= 9) | Installation of Single Package or Split System central unit w/ SEER ratings > or = 16, HSPF > or = 9 (split), 8.2 (single). Includes variable flow (VRF) systems. | ≤5.4 tons | ≥16 SEER, ≥9 HSPF (split), ≥8.2 HSPF (single) | Air source heat pumps | Only air source heat pumps <= 5.4 tons
x | HVAC - CI | Air Conditioning C&I - (<=5.4 Ton & SEER >= 16) | Unitary HVAC Equipment | WATER-COOLED AND EVAPORATIVE COOLING AIR CONDITIONERS | >11.25 to > 63.3 tons | Per Ton | 250 | Mid-Atlantic TRM, V10, Pg. 283 | Air Conditioning C&I - (<=5.4 Ton & SEER >= 16) | Installation of Single Package or Split System central units w/ SEER ratings > or = 16. Includes variable flow (VRF) systems. | ≤5.4 tons | ≥16 SEER | Water-cooled and evaporative cooled air conditioners | Possibly pair with rows 10,11,12
x | HVAC - CI | Air Conditioning C&I - ( >5.4 < 20 Ton, >=12 EER or>=13 IEER) | Unitary HVAC Equipment | WATER-COOLED AND EVAPORATIVE COOLING AIR CONDITIONERS | >11.25 to > 63.3 tons | Per Ton | 250 | Mid-Atlantic TRM, V10, Pg. 283 | Air Conditioning C&I - ( >5.4 < 20 Ton, >=12 EER or>=13 IEER) | Installation of a Single Package or Split System central unit exceeding the baselines in International Energy Conservation Code (IECC 2018) by 5%. Includes variable flow (VRF) systems. | >5.4 to <20 tons | Exceeds IECC 2018 by at least 5% | Water-cooled and evaporative cooled air conditioners
x | HVAC - CI | Air Conditioning C&I - (>=20 Ton, >=10.2 EER or >=11.4 IEER) | Unitary HVAC Equipment | WATER-COOLED AND EVAPORATIVE COOLING AIR CONDITIONERS | >11.25 to > 63.3 tons | Per Ton | 250 | Mid-Atlantic TRM, V10, Pg. 283 | Air Conditioning C&I - (>=20 Ton, >=10.2 EER or >=11.4 IEER) | Installation of a Single Package or Split System central unit exceeding the baselines in International Energy Conservation Code (IECC 2018) by 5%. Includes variable flow (VRF) systems. | ≥20 tons | Exceeds IECC 2018 by at least 5% | Water-cooled and evaporative cooled air conditioners
| HVAC - CI | Heat Pump C&I - (<=5.4 Ton & HSPF >= 9) | Unitary HVAC Equipment | WATER-COOLED AND EVAPORATIVE COOLING AIR CONDITIONERS | >11.25 to > 63.3 tons | Per Ton | 250 | Mid-Atlantic TRM, V10, Pg. 283 | Heat Pump C&I - (<=5.4 Ton & HSPF >= 9) | Installation of Single Package or Split System central unit w/ SEER ratings > or = 16, HSPF > or = 9 (split), 8.2 (single). Includes variable flow (VRF) systems. |  |  | Water-cooled and evaporative cooled air conditioners | duplicate of row 15 - can get rid of
| HVAC - CI | Air Conditioning C&I - (>=20 Ton, >=10.2 EER or >=11.4 IEER) | Unitary HVAC Equipment | WATER-COOLED AND EVAPORATIVE COOLING AIR CONDITIONERS | Air Source or Water Source Heat Pumps - all sizes | Per Ton | 250 | Mid-Atlantic TRM, V10, Pg. 283 | Air Conditioning C&I - (>=20 Ton, >=10.2 EER or >=11.4 IEER) | Installation of a Single Package or Split System central unit exceeding the baselines in International Energy Conservation Code (IECC 2018) by 5%. Includes variable flow (VRF) systems. |  |  | Water-cooled and evaporative cooled air conditioners
| HVAC - CI | Air Conditioning C&I - (<=5.4 Ton & SEER >= 16) | Unitary HVAC Equipment | WATER-COOLED AND EVAPORATIVE COOLING AIR CONDITIONERS | Air Source or Water Source Heat Pumps - all sizes | Per Ton | 250 | Mid-Atlantic TRM, V10, Pg. 283 | Air Conditioning C&I - (<=5.4 Ton & SEER >= 16) | Installation of Single Package or Split System central units w/ SEER ratings > or = 16. Includes variable flow (VRF) systems. |  |  | Water-cooled and evaporative cooled air conditioners
| HVAC - CI | Air Conditioning C&I - ( >5.4 < 20 Ton, >=12 EER or>=13 IEER) | Unitary HVAC Equipment | WATER-COOLED AND EVAPORATIVE COOLING AIR CONDITIONERS | Air Source or Water Source Heat Pumps - all sizes | Per Ton | 250 | Mid-Atlantic TRM, V10, Pg. 283 | Air Conditioning C&I - ( >5.4 < 20 Ton, >=12 EER or>=13 IEER) | Installation of a Single Package or Split System central unit exceeding the baselines in International Energy Conservation Code (IECC 2018) by 5%. Includes variable flow (VRF) systems. |  |  | Water-cooled and evaporative cooled air conditioners
| HVAC - CI | Heat Pump C&I - (<=5.4 Ton & HSPF >= 9) | Unitary HVAC Equipment | WATER-COOLED AND EVAPORATIVE COOLING AIR CONDITIONERS | Air Source or Water Source Heat Pumps - all sizes | Per Ton | 250 | Mid-Atlantic TRM, V10, Pg. 283 | Heat Pump C&I - (<=5.4 Ton & HSPF >= 9) | Installation of Single Package or Split System central unit w/ SEER ratings > or = 16, HSPF > or = 9 (split), 8.2 (single). Includes variable flow (VRF) systems. |  |  | Water-cooled and evaporative cooled air conditioners
| HVAC - CI | Heat Pumps C&I - Wtr & GeoT - ES Tier 3 (<=11.25 Tons & EER >= 17.1) | Unitary HVAC Equipment | WATER-COOLED AND EVAPORATIVE COOLING AIR CONDITIONERS | Air Source or Water Source Heat Pumps - all sizes | Per Ton | 250 | Mid-Atlantic TRM, V10, Pg. 284 |  | Installation of a Single Package or Split System central unit exceeding the baselines in International Energy Conservation Code (IECC 2018) by 5%. Includes variable flow (VRF) systems. | ≤11.25 tons | Exceeds IECC 2018 by at least 5% | Water source heat pumps | Water source heat pumps <=11.25 tons
| HVAC - CI | Heat Pumps C&I - Wtr & GeoT - ES Tier 3 (<=11.25 Tons & EER >= 17.1) | Unitary HVAC Equipment | GEOTHERMAL HEAT PUMPS | Geothermal Heat Pumps – (Ground Source/Ground Water Source) Tier I | Per Ton | 500 | Mid-Atlantic TRM, V10, Pg. 114 | Heat Pumps C&I - Wtr & GeoT - ES Tier 3 (<=11.25 Tons & EER >= 17.1) | Installation of Energy Star qualified Ground Source Heat Pump: The following scenarios are eligible: • Water to Air - Closed Loop: 17.1 EER, 3.6 COP; Open Loop: 21.1 EER, 4.1 COP • Water to Water - Closed Loop: 16.1 EER, 3.1 COP; Open Loop: 20.1 EER, 3.5 COP; Direct: 16 EER, 3.6 COP | ≤11.25 tons | Energy Star Tier I | Ground source heat pump | Figure out criteria for tier 1 and tier 2
| HVAC - CI | Heat Pumps C&I - Wtr & GeoT - ES Tier 3 (<=11.25 Tons & EER >= 17.1) | Unitary HVAC Equipment | GEOTHERMAL HEAT PUMPS | Geothermal Heat Pumps – (Ground Source/Ground Water Source) Tier II | Per Ton | 500 | Mid-Atlantic TRM, V10, Pg. 114 | Heat Pumps C&I - Wtr & GeoT - ES Tier 3 (<=11.25 Tons & EER >= 17.1) | Installation of Energy Star qualified Ground Source Heat Pump: The following scenarios are eligible: • Water to Air - Closed Loop: 17.1 EER, 3.6 COP; Open Loop: 21.1 EER, 4.1 COP • Water to Water - Closed Loop: 16.1 EER, 3.1 COP; Open Loop: 20.1 EER, 3.5 COP; Direct: 16 EER, 3.6 COP | ≤11.25 tons | Energy Star Tier II | Ground source heat pump | Just have customer select tier 1 and tier 2
| HVAC - CI | Ductless Mini-Split Heat Pump C&I (<5.4 Ton & >=9.0 HSPF) | Unitary HVAC Equipment | GEOTHERMAL HEAT PUMPS | Ductless, Mini Split Air Conditioners or Heat Pumps - all sizes | Per Ton | 150 | Mid-Atlantic TRM, V10, Pg 292 | Ductless Mini-Split Heat Pump C&I (<5.4 Ton & >=9.0 HSPF) | Purchase and installation of a new or replacement ENERGY STAR qualifying unit w/ SEER >= 20, EER >=13 or HSPF >= 10. | ≤5.4 tons | Energy Star qualified (SEER ≥ 20, EER ≥ 13 or HSPF ≥ 10)
x | HVAC - CI | PTAC C&I (SEER >=16) | Unitary HVAC Equipment | PACKAGED TERMINAL AIR CONDITIONERS OR HEAT PUMPS | <3/4 tons | Per Unit | 75 | Mid-Atlantic TRM, v10, Pg. 283 | PTAC C&I (SEER >=16) | Installation of packaged terminal unit exceeding rating in IECC 2018 by 7.5%. Includes variable flow (VRF) systems. | <3/4 tons | Exceeds IECC 2018 by at least 7.5% | PTAC & PTHP
x | HVAC - CI | PTAC C&I (SEER >=16) | Unitary HVAC Equipment | PACKAGED TERMINAL AIR CONDITIONERS OR HEAT PUMPS | ≥3/4 and <1 tons | Per Unit | 100 | Mid-Atlantic TRM, v10, Pg. 283 | PTAC C&I (SEER >=16) | Installation of packaged terminal unit exceeding rating in IECC 2018 by 7.5%. Includes variable flow (VRF) systems. | ≥3/4 and <1 tons | Exceeds IECC 2018 by at least 7.5% | PTAC & PTHP
x | HVAC - CI | PTAC C&I (SEER >=16) | Unitary HVAC Equipment | PACKAGED TERMINAL AIR CONDITIONERS OR HEAT PUMPS | ≥1 tons | Per Unit | 125 | Mid-Atlantic TRM, v10, Pg. 283 | PTAC C&I (SEER >=16) | Installation of packaged terminal unit exceeding rating in IECC 2018 by 7.5%. Includes variable flow (VRF) systems. | ≥1 tons | Exceeds IECC 2018 by at least 7.5% | PTAC & PTHP
x | HVAC - CI | PTHP C&I (HSPF >= 8.2) | Unitary HVAC Equipment | PACKAGED TERMINAL AIR CONDITIONERS OR HEAT PUMPS | <3/4 tons | Per Unit | 75 | Mid-Atlantic TRM, v10, Pg. 283 | PTHP C&I (HSPF >= 8.2) | Installation of packaged terminal unit exceeding rating in IECC 2018 by 7.5%. Includes variable flow (VRF) systems. | <3/4 tons | Exceeds IECC 2018 by at least 7.5% | PTAC & PTHP
x | HVAC - CI | PTHP C&I (HSPF >= 8.2) | Unitary HVAC Equipment | PACKAGED TERMINAL AIR CONDITIONERS OR HEAT PUMPS | ≥3/4 and <1 tons | Per Unit | 100 | Mid-Atlantic TRM, v10, Pg. 283 | PTHP C&I (HSPF >= 8.2) | Installation of packaged terminal unit exceeding rating in IECC 2018 by 7.5%. Includes variable flow (VRF) systems. | ≥3/4 and <1 tons | Exceeds IECC 2018 by at least 7.5% | PTAC & PTHP
x | HVAC - CI | PTHP C&I (HSPF >= 8.2) | Unitary HVAC Equipment | PACKAGED TERMINAL AIR CONDITIONERS OR HEAT PUMPS | ≥1 tons | Per Unit | 125 | Mid-Atlantic TRM, v10, Pg. 283 | PTHP C&I (HSPF >= 8.2) | Installation of packaged terminal unit exceeding rating in IECC 2018 by 7.5%. Includes variable flow (VRF) systems. | ≥1 tons | Exceeds IECC 2018 by at least 7.5% | PTAC & PTHP
x | HVAC - CI | HVAC - Custom C&I | Unitary HVAC Equipment | PACKAGED TERMINAL AIR CONDITIONERS OR HEAT PUMPS | Dual Enthalpy Economizer Controls | Per Unit | 250 | Mid-Atlantic TRM, v10, Pg. 283 | PTAC C&I (SEER >=16) | Installation of packaged terminal unit exceeding rating in IECC 2018 by 7.5%. Includes variable flow (VRF) systems. | N/A | N/A | Controls | Per controller, not per ton
x | HVAC - CI | HVAC - Custom C&I | Unitary HVAC Equipment | PACKAGED TERMINAL AIR CONDITIONERS OR HEAT PUMPS | Dual Enthalpy Economizer Controls | Per Unit | 250 | Mid-Atlantic TRM, v10, Pg. 283 | PTHP C&I (HSPF >= 8.2) | Installation of packaged terminal unit exceeding rating in IECC 2018 by 7.5%. Includes variable flow (VRF) systems. | N/A | N/A | Controls | Per controller, not per ton
x | Prescriptive - Custom | Custom - HVAC & Chillers | Chillers | Air Cooled Chiller | Air-Cooled Chiller with Condenser | Per Ton | 300 | Mid-Atlantic TRM, V10, Pg 302 | Custom - HVAC & Chillers | Replacement or new installation of an electric chiller with efficiency exceeding the baselines in International Energy Conservation Code 2018 (IECC 2018), Table C403.2.3(7), by 5%.
x | Prescriptive - Custom | Custom - HVAC & Chillers | Chillers | WATER-COOLED SCREW CHILLER & RECIPROCATING CHILLERS | < 75 tons | Per Ton | 300 | Mid-Atlantic TRM, V10, Pg 302 | Custom - HVAC & Chillers | Replacement or new installation of an electric chiller with efficiency exceeding the baselines in International Energy Conservation Code 2018 (IECC 2018), Table C403.2.3(7), by 5%.
x | Prescriptive - Custom | Custom - HVAC & Chillers | Chillers | WATER-COOLED SCREW CHILLER & RECIPROCATING CHILLERS | ≥ 75 tons and < 1000 tons | Per Ton | 300 | Mid-Atlantic TRM, V10, Pg 302 | Custom - HVAC & Chillers | Replacement or new installation of an electric chiller with efficiency exceeding the baselines in International Energy Conservation Code 2018 (IECC 2018), Table C403.2.3(7), by 5%.
x | Prescriptive - Custom | Custom - HVAC & Chillers | Chillers | WATER-COOLED CENTRIFUGAL CHILLERS | < 150 tons and < 300 tons | Per Ton | 300 | Mid-Atlantic TRM, V10, Pg 302 | Custom - HVAC & Chillers | Replacement or new installation of an electric chiller with efficiency exceeding the baselines in International Energy Conservation Code 2018 (IECC 2018), Table C403.2.3(7), by 5%.
x | Prescriptive - Custom | Custom - HVAC & Chillers | Chillers | WATER-COOLED CENTRIFUGAL CHILLERS | ≥ 300 tons and < 600 tons | Per Ton | 300 | Mid-Atlantic TRM, V10, Pg 302 | Custom - HVAC & Chillers | Replacement or new installation of an electric chiller with efficiency exceeding the baselines in International Energy Conservation Code 2018 (IECC 2018), Table C403.2.3(7), by 5%.
x | Prescriptive - Custom | Custom - HVAC & Chillers | Chillers | WATER-COOLED CENTRIFUGAL CHILLERS | ≥ 600 tons and ≤1000 tons | Per Ton | 300 | Mid-Atlantic TRM, V10, Pg 302 | Custom - HVAC & Chillers | Replacement or new installation of an electric chiller with efficiency exceeding the baselines in International Energy Conservation Code 2018 (IECC 2018), Table C403.2.3(7), by 5%.
x | HVAC - CI | Room Air Conditioner C&I (EER>=10.2) | COMMERICAL APPLIANCES | APPLIANCES | ENERGY STAR Room Air Conditioner | Per Unit | 25 | Mid-Atlantic TRM V10, Pg 70 | Room Air Conditioner C&I (EER>=10.2) | Purchase and installation of new unit meeting ENERGY STAR standard.
x | HVAC - CI | SMART Thermostat -Rebate | Unitary HVAC Equipment | OTHER HVAC EQUIPMENT | HVAC - Smart Thermostat | Per Unit | 100 | The purchase and installation of a smart thermostat that has earned ENERGY STAR certification and/or meets the requirements as outlined in applicable Mid-Atlantic/MD TRM. | Mid-Atlantic TRM, V10 Pg 319 | CHECK THIS - TK Eligible to small commercial customers with normal weekday occupancy and hours of use (please have customer provide), controlling one (1) split or single packaged system with a heat pump and/or air conditioner rated 5.4 tons (65,000 BTU/hr) or less. See EMPOWER Rate tab for eligibe customers.
Note on K41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: how to have customers provide HOU? Do we use these instead of hours in TRM? Reply: up to 25 tons, use EFLH

## Instructions
Calculator for HVAC Measures
***This calculator is used for estimating savings and incentives from the installation of HVAC measures. The measure inputs used in this calculator, by an applicant, will be reviewed by the Program in order to determine the final incentive amount. The Program reserves the right to inspect any and all measures prior to any incentive payment.
Input Instructions
White cells indicate that user input is required. Cells with an asterisk (*) are required.
Grey cells are calculated values.
Worksheet Summary
Summary
Summary of Equipment Cost, Calculator Savings, and Incentives
Methodology
Defines the methodology used for all measures in this workbook.
Air Conditioners
Calculates energy savings for air cooled, water cooled, and evaporatively cooled air conditioners.
Air Source Heat Pumps
Calculates energy savings for air source heat pumps <5.4 tons.
Ground Source and Water Source Heat Pumps (GSHP & WSHP)
Calculates energy savings for water source heat pumps, and ground source heat pumps meeting ENERGY STAR criteria and <11.25 tons.
Ductless Mini-Split Heat Pumps
Calculates energy savings for ductless mini-split heat pumps meeting ENERGY STAR criteria and <5.4 tons.
Packaged Terminal Air Conditioners and Heat Pumps (PTAC & PTHP)
Calculates energy savings for packaged terminal air conditioners and heat pumps.
Chillers
Calculates energy savings for air cooled and water cooled chillers.
Variable Frequency Drives (VFDs)
Calculates energy savings for installation of new VFD for an existing motor driving fans, pumps, and other suitable applications. VFD retrofits
are not eligible.
SMART Thermostat
Calculates energy savings for installation of smart thermostat meeting ENERGY STAR criteria and ≤25 tons.
Room Air Conditioner
Calculates energy savings for room air conditioners meeting ENERGY STAR criteria.
ECM Circulating Fan
Calculates energy savings for ECM circulating fans.
ECM Circulator Pump
Calculates energy savings for ECM circulator pumps.
Version Log
The Version Log Worksheet tracks updates and changes made to the workbook.

## Methodology (hidden)
Calculator Methodology
Smart Thermostat
Energy savings calculation based on Maryland TRM V10.
Thermostats must meet following requirements:
Must be installed to control central A/C, heat pump, furnace, or rooftop units (RTUs) with capacity up to 65,000 BTU/h.
Must serve normal conditioned spaces, not semi-conditioned spaces or spaces with large frequently open doors (e.g. loading docks and car repair shops).
If manually operated non-programmable thermostat baseline is claimed, supporting photographic documentation is required.
HVAC VFD Applications
Energy savings calculation based on Maryland TRM V10.
The application must have a load that varies and proper controls must be installed. This measure is for HVAC applications only.
The baseline condition is a motor, 200 hp or less, without a VFD control.
Energy Savings for HVAC fans are calculated as
Demand savings for HVAC fans are calculated as
Where the Part Load Ratio value at 100% is used for the peak.
Energy Savings for Pumps are calculated as
Demand Savings for Pumps are calculated as
Air Conditioners
Energy savings calculation based on Maryland TRM V10. This measure documents savings associated with the installation of new heating, ventilating, and air conditioning systems exceeding baseline efficiency criteria in place of an existing system or a new standard efficiency system of the same capacity.
Energy savings for air-, water-, and evaporatively-cooled unitary ACs and PTACs
Time of Sale:
Early Replacement:
Heat Pumps
Energy savings calculation based on Maryland TRM V10. This measure documents savings associated with the installation of new heating, ventilating, and air conditioning systems exceeding baseline efficiency criteria in place of an existing system or a new standard efficiency system of the same capacity.
Energy savings for air-source HPs and PTHPs
Time of Sale:
Early Replacement:
Energy savings for water-source and ground-source heat pumps
Energy savings for ductless mini-split heat pumps
Δ𝑘𝑊ℎ=(0.746 𝑘𝑊/𝐻𝑃∗𝐻𝑃∗𝐿𝐹/𝜂_𝑚𝑜𝑡𝑜𝑟 )∗𝑅𝐻𝑅𝑆∗𝑄𝑡𝑦 ∗[∑_(0%)^(100%)▒〖(%𝐹𝐹∗𝑃𝐿𝑅_𝐵𝑎𝑠𝑒 )−∑_(0%)^(100%)▒(%𝐹𝐹∗𝑃𝐿𝑅_𝑅𝑒𝑡𝑟𝑜 ) 〗]
Δ𝑘𝑊=(0.746 𝑘𝑊/𝐻𝑃∗𝐻𝑃∗𝐿𝐹/𝜂_𝑚𝑜𝑡𝑜𝑟 )∗𝑄𝑡𝑦 ∗(𝑃𝐿𝑅_(𝐵𝑎𝑠𝑒,𝑃𝑒𝑎𝑘)−𝑃𝐿𝑅_(𝑅𝑒𝑡𝑟𝑜,𝑃𝑒𝑎𝑘) )
Δ𝑘𝑊ℎ=(0.746 𝑘𝑊/𝐻𝑃∗𝐻𝑃∗𝐿𝐹/𝜂_𝑚𝑜𝑡𝑜𝑟 )∗𝑅𝐻𝑅𝑆∗𝑄𝑡𝑦 ∗𝐸𝑆𝐹
Δ𝑘𝑊=(0.746 𝑘𝑊/𝐻𝑃∗𝐻𝑃∗𝐿𝐹/𝜂_𝑚𝑜𝑡𝑜𝑟 )∗𝑄𝑡𝑦 ∗𝐷𝑆𝐹

## Summary
|  |  |  | Version: | 6.01
|  |  |  | Last Updated: | 2024-03-25
Date
Site Address | Total Incentive ($) | Total Equipment Cost ($) | Total Energy Savings (kWh) | Total Summer Peak Demand (kW) | Total Winter Peak Demand (kW) | Total Fossil Fuel (MMBtu/yr)
Building Type | 0 | 0 | 0 | 0 | 0 | 0
Total Project Cost
| Measure Name | Equipment Cost | Savings |  |  |  | Incentive
|  |  | kWh | Summer kW | Winter kW | Fossil Fuel Savings (MMBtu/yr)
| Air Conditioners | 0 | 0 | 0 | 0 | 0 | 0
| Air Source Heat Pumps | 0 | 0 | 0 | 0 | 0 | 0
| GSHP & WSHP | 0 | 0 | 0 | 0 | 0 | 0
| Ductless Mini-Splits | 0 | 0 | 0 | 0 | 0 | 0
| PTACs & PTHPs | 0 | 0 | 0 | 0 | 0 | 0
| Chillers | 0 | 0 | 0 | 0 | 0 | 0
| VFDs | 0 | 0 | 0 | 0 | 0 | 0
| Smart Thermostats | 0 | 0 | 0 | 0 | 0 | 0
| Room ACs | 0 | 0 | 0 | 0 | 0 | 0
| ECM Circulating Fan | 0 | 0 | 0 | 0 | 0 | 0
| ECM Circulator Pump | 0 | 0 | 0 | 0 | 0 | 0

## Air Conditioners
Air Conditioners
| Instructions: Enter the project information in the white cells below. Energy savings calculation based on Maryland TRM V11. This measure documents savings associated with the installation of new heating, ventilating, and air conditioning systems exceeding baseline efficiency criteria in place of an existing system or a new standard efficiency system of the same capacity. | [6 empty] | Energy Savings (kWh/yr) | Summer Peak Demand Savings (kW) | Winter Peak Demand Savings (kW)
[8 empty] | 0 | 0 | 0
Date
Project Site
Building Type
Total Cost
| Project Type | Project Type | Installed Equipment | [5 empty] | Cooling | [5 empty] | Heating | Equipment Cost | Removed Equipment |  | Cooling |  |  |  | New Construction Baseline |  |  |  | EE Efficiency | Savings Factors |  |  |  | NC or ER Baseline |  | Qualifying Efficiency |  |  | Savings Calcs
|  |  | Manufacturer | Model | AHRI Certified Reference Number | Equipment Type* | Subcategory | Quantity | Nominal Tons | AHRI Rated Capacity (Btu/h) | EER | IEER/SEER/SEER2 | SEER / SEER2 | Single/Three Phase | Heating Type |  | Model # / Equipment Notes | Equipment Age (Years) | AHRI Rated Capacity (Btu/h) | EER | IEER/SEER/SEER2 | SEER/SEER2 | Size Category | Name Index | EER | IEER/SEER2 | SEER2 | EFLH cool | ETDF Bldg Type | ETDF Summer | ETDF Winter | EER base | IEER/SEER2 base | EER | IEER/SEER2 | Flag | ΔkWh cool | kW Summer Peak Savings | kW Winter Peak Savings | Incentives
1 | [32 empty] | FALSE |  |  |  | 0 |  | 0 | 0
2 | [32 empty] | FALSE |  |  |  | 0 |  | 0 | 0
3 | [32 empty] | FALSE |  |  |  | 0 |  | 0 | 0
4 | [32 empty] | FALSE |  |  |  | 0 |  | 0 | 0
5 | [32 empty] | FALSE |  |  |  | 0 |  | 0 | 0
6 | [32 empty] | FALSE |  |  |  | 0 |  | 0 | 0
7 | [32 empty] | FALSE |  |  |  | 0 |  | 0 | 0
8 | [32 empty] | FALSE |  |  |  | 0 |  | 0 | 0
9 | [32 empty] | FALSE |  |  |  | 0 |  | 0 | 0
10 | [32 empty] | FALSE |  |  |  | 0 |  | 0 | 0
Maryland TRM V11 - p.120

## Air Source Heat Pumps
Air Source Heat Pumps
| Instructions: Enter the project information in the white cells below. Energy savings calculation based on Maryland TRM V11. This measure documents savings associated with the installation of new heating, ventilating, and air conditioning systems exceeding baseline efficiency criteria in place of an existing system or a new standard efficiency system of the same capacity. | [10 empty] | Energy Savings (kWh/yr) | Summer Peak Demand Savings (kW) | Winter Peak Demand Savings (kW)
[12 empty] | 0 | 0 | 0
Date
Project Site
Building Type
Total Cost
| Project Type | Project Type | Installed Equipment | [7 empty] | Cooling |  |  | Heating |  |  | Equipment Cost | Removed Equipment |  | Cooling |  | Heating |  | Units | New Construction Baseline |  |  |  |  | EE Efficiency |  | Savings Factors |  |  |  |  | NC or ER Baseline |  |  | Qualifying Efficiency |  |  | Savings Calcs
|  |  | Manufacturer | Model | AHRI Certified Reference Number | Cold Climate? | Subcategory | Quantity | Units | Single/Three Phase | Nominal Tons | AHRI Rated Capacity (Btu/h) | SEER / SEER2 | Heating Type | AHRI Rated Capacity (Btu/h) | HSPF / HSPF2 |  | Model # / Equipment Notes | Equipment Age (Years) | AHRI Rated Capacity (Btu/h) | SEER/SEER2 | AHRI Rated Capacity (Btu/h) | HSPF/HSPF2 |  | Size Category | Name Index | EER2 | SEER2 | HSPF2 | SEER2 | HSPF2 | EFLH cool | EFLH heat | ETDF Bldg Type | ETDF Summer | ETDF Winter | EER base | SEER2 base | HSPF base | SEER2 | HSPF2 | Flag | ΔkWh cool | ΔkWh heat | ΔkWh total | kW Summer Peak Savings | kW Winter Peak Savings | Incentives
1 | [37 empty] | FALSE | FALSE | [5 empty] | 0 |  | 0 | 0
2 | [37 empty] | FALSE | FALSE | [5 empty] | 0 |  | 0 | 0
3 | [37 empty] | FALSE | FALSE | [5 empty] | 0 |  | 0 | 0
4 | [37 empty] | FALSE | FALSE | [5 empty] | 0 |  | 0 | 0
5 | [37 empty] | FALSE | FALSE | [5 empty] | 0 |  | 0 | 0
6 | [37 empty] | FALSE | FALSE | [5 empty] | 0 |  | 0 | 0
7 | [37 empty] | FALSE | FALSE | [5 empty] | 0 |  | 0 | 0
8 | [37 empty] | FALSE | FALSE | [5 empty] | 0 |  | 0 | 0
9 | [37 empty] | FALSE | FALSE | [5 empty] | 0 |  | 0 | 0
10 | [37 empty] | FALSE | FALSE | [5 empty] | 0 |  | 0 | 0
Maryland TRM V11 - p. 120
Note on AH12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: If split, lookup value for ducted. If packaged, look up packaged.
Note on AI12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: If split, lookup value for ducted. If packaged, look up packaged.

## GSHP (hidden)
Ground Source and Water Source Heat Pumps
| Instructions: Enter the project information in the yellow cells below. Energy savings calculation based on Maryland TRM V11. This measure documents savings associated with the installation of new heating, ventilating, and air conditioning systems exceeding baseline efficiency criteria in place of an existing system or a new standard efficiency system of the same capacity. | [7 empty] | Energy Savings (kWh/yr) | Demand Savings (kW)
[9 empty] | 0 | 0
Date
Project Site
Building Type
Total Cost
| Project Type | Installed Equipment | [8 empty] | Domestic Hot Water |  | Cooling |  |  | Heating |  |  | Equipment Cost | Baseline |  | Savings Factors | [5 empty] | Qualifying Efficiency |  |  | DHW |  |  | Savings Calcs
|  | Manufacturer | Model | AHRI Certified Reference Number | Energy Star Certified | Equipment Type | Name Manager | Subcategory | Quantity | Is Desuperheater used? | Is DHW electrically heated? | Electric Water Heater Size (Gallons) | Nominal Tons | AHRI Rated Capacity (Btu/h) | EER | Heating Type | AHRI Rated Capacity (Btu/h) | COP |  | SEER | HSPF | FLH cool | FLH heat | ETDFsummer cooling | ETDFwinter Electric Heating | ETDF Water Heating summer | ETDF Water Heating winter | EER | COP | Flag | ElecDHW | % DHW Displaced | UEF | ΔkWh cool | ΔkWh heat | kWh DHW | ΔkWh total | ΔkW Summer Peak | ΔkW Winter Peak | Incentives
1 | [19 empty] | 14 | 8.2 | 712 | 885 | 0.0007767 | 0.0007133 | 8.98e-05 | 0.0001731 |  |  |  | 0 | 0% | 0.9307 | 0 | 0 |  | 0 |  |  | 0
2 | [19 empty] | 14 | 8.2 | 712 | 885 | 0.0007767 | 0.0007133 | 8.98e-05 | 0.0001731 |  |  |  | 0 | 0% | 0.9307 | 0 | 0 |  | 0 |  |  | 0
3 | [19 empty] | 14 | 8.2 | 712 | 885 | 0.0007767 | 0.0007133 | 8.98e-05 | 0.0001731 |  |  |  | 0 | 0% | 0.9307 | 0 | 0 |  | 0 |  |  | 0
4 | [19 empty] | 14 | 8.2 | 712 | 885 | 0.0007767 | 0.0007133 | 8.98e-05 | 0.0001731 |  |  |  | 0 | 0% | 0.9307 | 0 | 0 |  | 0 |  |  | 0
5 | [19 empty] | 14 | 8.2 | 712 | 885 | 0.0007767 | 0.0007133 | 8.98e-05 | 0.0001731 |  |  |  | 0 | 0% | 0.9307 | 0 | 0 |  | 0 |  |  | 0
6 | [19 empty] | 14 | 8.2 | 712 | 885 | 0.0007767 | 0.0007133 | 8.98e-05 | 0.0001731 |  |  |  | 0 | 0% | 0.9307 | 0 | 0 |  | 0 |  |  | 0
7 | [19 empty] | 14 | 8.2 | 712 | 885 | 0.0007767 | 0.0007133 | 8.98e-05 | 0.0001731 |  |  |  | 0 | 0% | 0.9307 | 0 | 0 |  | 0 |  |  | 0
8 | [19 empty] | 14 | 8.2 | 712 | 885 | 0.0007767 | 0.0007133 | 8.98e-05 | 0.0001731 |  |  |  | 0 | 0% | 0.9307 | 0 | 0 |  | 0 |  |  | 0
9 | [19 empty] | 14 | 8.2 | 712 | 885 | 0.0007767 | 0.0007133 | 8.98e-05 | 0.0001731 |  |  |  | 0 | 0% | 0.9307 | 0 | 0 |  | 0 |  |  | 0
10 | [19 empty] | 14 | 8.2 | 712 | 885 | 0.0007767 | 0.0007133 | 8.98e-05 | 0.0001731 |  |  |  | 0 | 0% | 0.9307 | 0 | 0 |  | 0 |  |  | 0
Maryland Res TRM V11 - p. 101

## GSHP & WSHP
Ground Source and Water Source Heat Pumps
| Instructions: Enter the project information in the white cells below. Energy savings calculation based on Pennsylvania TRM V3. This measure documents savings associated with the installation of new heating, ventilating, and air conditioning systems exceeding baseline efficiency criteria in place of an existing system or a new standard efficiency system of the same capacity. | [9 empty] | Energy Savings (kWh/yr) | Demand Savings (kW)
[11 empty] | 0 | 0
Date
Project Site
Building Type
Total Cost
| Project Type | Project Type | Installed Equipment | [9 empty] | Cooling |  |  | Heating |  |  | Equipment Cost | Removed Equipment |  |  |  | Cooling |  | Heating |  | New Construction Baseline |  |  |  | Savings Factors |  |  |  | NC or ER Baseline |  |  |  | WSHP/GSHP Tier 1 |  | GSHP Tier 2 |  | Qualifying Efficiency |  | Savings Calcs
|  |  | Manufacturer | Model | AHRI Certified Reference Number | Energy Star Certified | Equipment Type | Name Manager | Subcategory | Quantity | Pump Motor HP | Pump Motor Efficiency | Nominal Tons | AHRI Rated Capacity (Btu/h) | EER | Heating Type | AHRI Rated Capacity (Btu/h) | COP |  | Model # / Equipment Notes | Equipment Age (Years) | Pump Motor HP | Pump Motor Efficiency | AHRI Rated Capacity (Btu/h) | EER | AHRI Rated Capacity (Btu/h) | COP | Size Category | Name Index | EER | COP | EFLH cool | EFLH heat | CF PJM | CF SSP | EER base | COP base | Pump Motor HP base | Pump Motor Efficiency base | EER | COP | EER | COP | Tier | Flag | ΔkWh cool | ΔkWh heat | kWh pump | ΔkWh total | ΔkW cool | ΔkW pump | ΔkW PJM | ΔkW SSP | Incentives
1 | [33 empty] | 0.66 | 0.69 |  |  |  | 0% | [9 empty] | 0 |  |  |  |  | 0
2 | [33 empty] | 0.66 | 0.69 |  |  |  | 0% | [9 empty] | 0 |  |  |  |  | 0
3 | [33 empty] | 0.66 | 0.69 |  |  |  | 0% | [9 empty] | 0 |  |  |  |  | 0
4 | [33 empty] | 0.66 | 0.69 |  |  |  | 0% | [9 empty] | 0 |  |  |  |  | 0
5 | [33 empty] | 0.66 | 0.69 |  |  |  | 0% | [9 empty] | 0 |  |  |  |  | 0
6 | [33 empty] | 0.66 | 0.69 |  |  |  | 0% | [9 empty] | 0 |  |  |  |  | 0
7 | [33 empty] | 0.66 | 0.69 |  |  |  | 0% | [9 empty] | 0 |  |  |  |  | 0
8 | [33 empty] | 0.66 | 0.69 |  |  |  | 0% | [9 empty] | 0 |  |  |  |  | 0
9 | [33 empty] | 0.66 | 0.69 |  |  |  | 0% | [9 empty] | 0 |  |  |  |  | 0
10 | [33 empty] | 0.66 | 0.69 |  |  |  | 0% | [9 empty] | 0 |  |  |  |  | 0
Pennsylvania TRM V3 - p.58

## Ductless Mini Splits
Ductless Mini-Split Heat Pumps
| Instructions: Enter the project information in the white cells below. Energy savings calculation based on Maryland TRM V11. This measure documents savings associated with the installation of new heating, ventilating, and air conditioning systems exceeding baseline efficiency criteria in place of an existing system or a new standard efficiency system of the same capacity. | [8 empty] | Energy Savings (kWh/yr) | Summer Peak Demand Savings (kW) | Winter Peak Demand Savings (kW)
[10 empty] | 0 | 0 | 0
Date
Project Site
Building Type
Total Cost
| Project Type | Installed Equipment | [6 empty] | Cooling |  |  |  | Heating |  |  | Equipment Cost | Baseline efficiency |  |  | Installed Unit Efficiency, converted to EER2/SEER2/HSPF2 |  |  | Savings Factors | [5 empty] | Qualifying Efficiency
|  | Manufacturer | Model | AHRI Certified Reference Number | Energy Star Certified | Quantity | Equipment Type | Units | Nominal Tons | AHRI Rated Capacity (Btu/h) | EER / EER2 | SEER / SEER2 | Heating Type | AHRI Rated Capacity (Btu/h) | HSPF / HSPF2 |  | EER2 | SEER2 | HSPF2 | EER2 | SEER2 | HSPF2 | EFLH cool | EFLH heat | ISR | ETDF Bldg Type | ETDF summer | ETDF winter | EER2 | SEER2 | HSPF2 | Qualifying Flag | ΔkWh cool | ΔkWh heat | ΔkWh total | ΔkW Summer Peak | ΔkW Winter Peak | Incentives
1 | [16 empty] | 10.5 | 14.3 | 7.5 | 0 | 0 | 0 |  |  | 1 |  |  |  | 11.2 | 15.2 | 7.8 |  |  |  | 0 |  |  | 0
2 | [16 empty] | 10.5 | 14.3 | 7.5 | 0 | 0 | 0 |  |  | 1 |  |  |  | 11.2 | 15.2 | 7.8 |  |  |  | 0 |  |  | 0
3 | [16 empty] | 10.5 | 14.3 | 7.5 | 0 | 0 | 0 |  |  | 1 |  |  |  | 11.2 | 15.2 | 7.8 |  |  |  | 0 |  |  | 0
4 | [16 empty] | 10.5 | 14.3 | 7.5 | 0 | 0 | 0 |  |  | 1 |  |  |  | 11.2 | 15.2 | 7.8 |  |  |  | 0 |  |  | 0
5 | [16 empty] | 10.5 | 14.3 | 7.5 | 0 | 0 | 0 |  |  | 1 |  |  |  | 11.2 | 15.2 | 7.8 |  |  |  | 0 |  |  | 0
6 | [16 empty] | 10.5 | 14.3 | 7.5 | 0 | 0 | 0 |  |  | 1 |  |  |  | 11.2 | 15.2 | 7.8 |  |  |  | 0 |  |  | 0
7 | [16 empty] | 10.5 | 14.3 | 7.5 | 0 | 0 | 0 |  |  | 1 |  |  |  | 11.2 | 15.2 | 7.8 |  |  |  | 0 |  |  | 0
8 | [16 empty] | 10.5 | 14.3 | 7.5 | 0 | 0 | 0 |  |  | 1 |  |  |  | 11.2 | 15.2 | 7.8 |  |  |  | 0 |  |  | 0
9 | [16 empty] | 10.5 | 14.3 | 7.5 | 0 | 0 | 0 |  |  | 1 |  |  |  | 11.2 | 15.2 | 7.8 |  |  |  | 0 |  |  | 0
10 | [16 empty] | 10.5 | 14.3 | 7.5 | 0 | 0 | 0 |  |  | 1 |  |  |  | 11.2 | 15.2 | 7.8 |  |  |  | 0 |  |  | 0
Maryland TRM V11 - p. 81

## PTAC & PTHP
PTAC/PTHP
| Instructions: Enter the project information in the white cells below. Energy savings calculation based on Maryland TRM V11. This measure documents savings associated with the installation of new heating, ventilating, and air conditioning systems exceeding baseline efficiency criteria in place of an existing system or a new standard efficiency system of the same capacity. | [6 empty] | Energy Savings (kWh/yr) | Summer Peak Demand Savings (kW) | Winter Peak Demand Savings (kW)
[8 empty] | 0 | 0 | 0
Date
Project Site
Building Type
Total Cost
| Project Type | Project Type | Installed Equipment | [7 empty] | Cooling |  |  | Heating |  |  | Equipment Cost | Removed Equipment |  | Cooling |  | Heating |  | NC Baseline |  |  | Savings Factors |  |  |  |  | NC or ER baseline |  | Qualifying Efficiency |  |  | Savings Calcs
|  |  | Manufacturer | Model | AHRI Certified Reference Number | Equipment Type | Size Category | Height (in) | Width (in) | Quantity | Nominal Tons | AHRI Rated Capacity (Btu/h) | EER | Heating Type | AHRI Rated Capacity (Btu/h) | COP |  | Model # / Equipment Notes | Equipment Age (Years) | AHRI Rated Capacity (Btu/h) | EER | AHRI Rated Capacity (Btu/h) | COP | Capacity for EER baseline calc | EER | COP | EFLH cool | EFLH heat | ETDF Bldg Type | ETDF summer | ETDF winter | EER base | COP base | EER | COP | Flag | ΔkWh cool | ΔkWh heat | ΔkWh total | ΔkW Summer Peak | ΔkW Winter Peak | Incentives
1 | [23 empty] | 7000 | [14 empty] | 0 |  | 0 | 0
2 | [23 empty] | 7000 | [14 empty] | 0 |  | 0 | 0
3 | [23 empty] | 7000 | [14 empty] | 0 |  | 0 | 0
4 | [23 empty] | 7000 | [14 empty] | 0 |  | 0 | 0
5 | [23 empty] | 7000 | [14 empty] | 0 |  | 0 | 0
6 | [23 empty] | 7000 | [14 empty] | 0 |  | 0 | 0
7 | [23 empty] | 7000 | [14 empty] | 0 |  | 0 | 0
8 | [23 empty] | 7000 | [14 empty] | 0 |  | 0 | 0
9 | [23 empty] | 7000 | [14 empty] | 0 |  | 0 | 0
10 | [23 empty] | 7000 | [14 empty] | 0 |  | 0 | 0
Maryland TRM V11 - p. 120

## Chillers
Chillers
| Instructions: Enter the project information in the white cells below. Energy savings calculation based on Maryland TRM V11. This measure documents savings associated with the installation of a new high efficiency electric water chilling package for HVAC in place of existing chiller or a new standard efficiency chiller of the same capacity. Note: This measure only applies to single chillers. Process chillers and multiple chiller configurations must go through the custom program. | [7 empty] | Energy Savings (kWh/yr) | Summer Peak Demand Savings (kW) | Winter Peak Demand Savings (kW)
[9 empty] | 0 | 0 | 0
Date
Project Site
Building Type
Total Cost
| Project Type | Project Type | Installed Equipment | [5 empty] | Cooling |  |  |  |  | Equipment Cost | Removed Equipment |  | Cooling |  |  | New Construction Baseline |  |  |  | Savings Factors |  |  |  | NC or ER Baseline |  | Qualifying Efficiency |  |  | Performance Incentive |  | Savings Calcs
|  |  | Manufacturer | Model | AHRI Certified Reference Number | Equipment Type | Compressor Control Type | Quantity | Nominal Tons | AHRI Rated Capacity (Tons) | Compliance Path | Full Load | IPLV |  | Model # / Equipment Notes | Equipment Age (Years) | AHRI Rated Capacity (Tons) | Full Load | IPLV | Size Category | Name Index | Full Load | IPLV | EFLH | ETDF Bldg Type | ETDF Summer | ETDF Winter | Full Load base | IPLV base | Full Load | IPLV | Flag | Full Load multiplier | IPLV multiplier | ΔkWh | kW Summer Peak Savings | kW Winter Peak Savings | Incentives
1 | [32 empty] | #VALUE! | #VALUE! | 0 |  | 0 | 0
2 | [32 empty] | #VALUE! | #VALUE! | 0 |  | 0 | 0
3 | [32 empty] | #VALUE! | #VALUE! | 0 |  | 0 | 0
4 | [32 empty] | #VALUE! | #VALUE! | 0 |  | 0 | 0
5 | [32 empty] | #VALUE! | #VALUE! | 0 |  | 0 | 0
6 | [32 empty] | #VALUE! | #VALUE! | 0 |  | 0 | 0
7 | [32 empty] | #VALUE! | #VALUE! | 0 |  | 0 | 0
8 | [32 empty] | #VALUE! | #VALUE! | 0 |  | 0 | 0
9 | [32 empty] | #VALUE! | #VALUE! | 0 |  | 0 | 0
10 | [32 empty] | #VALUE! | #VALUE! | 0 |  | 0 | 0
Maryland TRM V11 - p. 94

## VFDs
HVAC VFD Calculator
| Instructions: Enter the project information in the white cells below. See Instructions Worksheet for more information. Must enter building type. | [5 empty] | Energy Savings (kWh/yr) | Summer Peak Demand Savings (kW) | Winter Peak Demand Savings (kW)
[7 empty] | 0 | 0 | 0
Date
Project Site
Building Type
Total Cost
| Project Type | Motor Application | Manufacturer | Model | Baseline Fan Control Type | Retrofit Fan Control Type | Motor Quantity | Motor HP | Nameplate Motor Efficiency | Equipment Cost | RHRS Base | Σ(%FF x PLRbase) | Σ(%FF x PLRret) | PLRbase | PLRret | Energy Savings Factor (ESF) | ETDF Bldg Type | ETDF Summer | ETDF Winter | Motor Application Data Export | Existing Flow Control Data Export | Efficient Flow Control Data Export | Energy Savings | kW Summer Peak Savings | kW Winter Peak Savings | Incentive
1 | [22 empty] | 0 |  | 0 | 0
2 | [22 empty] | 0 |  | 0 | 0
3 | [22 empty] | 0 |  | 0 | 0
4 | [22 empty] | 0 |  | 0 | 0
5 | [22 empty] | 0 |  | 0 | 0
6 | [22 empty] | 0 |  | 0 | 0
7 | [22 empty] | 0 |  | 0 | 0
8 | [22 empty] | 0 |  | 0 | 0
9 | [22 empty] | 0 |  | 0 | 0
10 | [22 empty] | 0 |  | 0 | 0
Maryland TRM V11 - p. 131

## Smart Thermostat Lookup (hidden)
Installation Type
Retrofit
New Construction
Retrofit
Manually Operated - Photographs required
Programmable Thermostat
Unknown
Savings Factors | ElecCool Saving % | ElecHeat Saving % | FuelHeat Saving %
Manually Operated - Photographs required | 9.2% | 5.2% | 1.3%
Programmable Thermostat | 9.2% | 5.2% | 1.3%
New Construction | 11.5% | 4.8% | 0.6%
HVAC Unit Type Controlled | Heating Type
None | None
Air Source Heat Pump | Air Source Heat Pump
Air Source Air Conditioner | Electric Resistance
Water Cooled Air Conditioner | Non-Electric
Space Type
Normal Conditioned
Semi-Conditioned
Space with Large Frequently Opened Doors
ISR
1
Incentive Per Unit
100

## Smart Thermostat
Smart Thermostat
| Instructions: Enter the project information in the white cells below. See Instructions Worksheet for more information. Eligible to small commercial customers with normal weekday occupancy and hours of use, controlling (1) split or single packaged system with heat pump or air conditioner rated 25 Tons (300,000 BTU/hr) or less. | [6 empty] | Energy Savings (kWh/yr) | Summer Peak Demand Savings (kW) | Winter Peak Demand Savings (kW) | Fossil Fuel Savings (MMBtu/yr)
[8 empty] | 0 | 0 | 0 | 0
Date
Project Site
Building Type
Total Cost
| Project Type | Project Type | Manufacturer | Model | Existing Thermostat Type | Smart Thermostat Quantity | Air Conditioning Type | HVAC Unit Cooling Capacity (Btu/h) | SEER / IEER | Heating Type | HVAC Unit Heating Capacity (Btu/h) | HSPF or COP | Heating Capacity of Furnace (Btu/h) | AFUE of controlled unit | Material Cost ($) | Cooling Size Category | Cooling Name Index | Heating Size Category | Heating Name Index | EFLHcool | EFLH Heat | Electric Cool Saving % | Energy Savings (kWh) cooling | Elec Heat Saving % | Energy Savings (kWh) heating | Fuel Heat Saving % | MMBtu Savings | Total Energy Savings (kWh/yr) | Incentive ($) | ETDF Bldg Type | ETDF Summer | ETDF Winter | kW Summer Peak Savings | kW Winter Peak Savings
1 | [22 empty] | 0 | [5 empty] | 0
2 | [22 empty] | 0 | [5 empty] | 0
3 | [22 empty] | 0 | [5 empty] | 0
4 | [22 empty] | 0 | [5 empty] | 0
5 | [22 empty] | 0 | [5 empty] | 0
6 | [22 empty] | 0 | [5 empty] | 0
7 | [22 empty] | 0 | [5 empty] | 0
8 | [22 empty] | 0 | [5 empty] | 0
9 | [22 empty] | 0 | [5 empty] | 0
10 | [22 empty] | 0 | [5 empty] | 0
Maryland TRM V11 - p. 100
might need two separate columns for HSPF and COP to export

## Room AC
Room Air Conditioners
| Instructions: Enter the project information in the white cells below. Energy savings calculation based on Maryland TRM V11. This measure documents savings associated with the installation of new heating, ventilating, and air conditioning systems exceeding baseline efficiency criteria in place of an existing system or a new standard efficiency system of the same capacity. | [6 empty] | Energy Savings (kWh/yr) | Summer Peak Demand Savings (kW) | Winter Peak Demand Savings (kW)
[8 empty] | 0 | 0 | 0
Date
Project Site
Building Type
Total Cost
| Project Type | Project Type | Installed Equipment | [5 empty] | Cooling |  | Equipment Cost | Removed Equipment |  | Cooling |  |  | New Construction Baseline |  |  |  | Savings Factors |  |  |  | NC or ER | Qualifying Efficiency |  | Savings Calcs
|  |  | Manufacturer | Model | Equipment Type | Subcategory | Connected to Network | Quantity | Rated Capacity (Btu/h) | CEER |  | Model # / Equipment Notes | Equipment Age (Years) | Rated Capacity (Btu/h) | EER | CEER | Size Category | Name Index | Data Export | CEER | Hours | ETDF Bldg Type | ETDF Summer | ETDF Winter | CEER Base | CEER | Flag | ΔkWh cool | ΔkW Peak Summer | ΔkW Peak Winter | Incentives
1 | [20 empty] | 168 | [6 empty] | 0 |  | 0 | 0
2 | [20 empty] | 168 | [6 empty] | 0 |  | 0 | 0
3 | [20 empty] | 168 | [6 empty] | 0 |  | 0 | 0
4 | [20 empty] | 168 | [6 empty] | 0 |  | 0 | 0
5 | [20 empty] | 168 | [6 empty] | 0 |  | 0 | 0
6 | [20 empty] | 168 | [6 empty] | 0 |  | 0 | 0
7 | [20 empty] | 168 | [6 empty] | 0 |  | 0 | 0
8 | [20 empty] | 168 | [6 empty] | 0 |  | 0 | 0
9 | [20 empty] | 168 | [6 empty] | 0 |  | 0 | 0
10 | [20 empty] | 168 | [6 empty] | 0 |  | 0 | 0
Maryland TRM Res V11 - p. 138

## ECM Circulating Fan
ECM Circulating Fan
Instructions: Enter the project information in the white cells below. Energy savings calculation based on Maryland TRM V11. This measure documents savings associated with the replacement of existing shaded-pole (SP) or permanent-split capacitor (PSC) circulator fan motors in an air handling unit with an electronically commutated motor (ECM). This measure applies only to circulating fan motors of 1hp or less. Additionally, new construction and replace-on-burnout vintages are not eligible to participate, as ECM technology is required in new equipment by federal efficiency standards.
|  |  |  | Energy Savings (kWh/yr) | Summer Peak Demand Savings (kW) | Winter Peak Demand Savings (kW)
|  |  |  | 0 | 0 | 0
Date
Project Site
Building Type
Total Cost
| Project Type | Fan Quantity | Baseline Fan Horsepower (hp) | Baseline Fan Motor Type | ECM Fan Horsepower (hp) | Equipment Cost
1
2
3
4
5
6
7
8
9
10
Maryland TRM V11 - p. 87

## ECM Circulator Pump
ECM Circulator Pump
Instructions: Enter the project information in the white cells below. Energy savings calculation based on Maryland TRM V11. This measure documents savings associated with replacing single-speed induction motor circulator pumps with electronically commutated motor (ECM) - also called brushless permanent magnet (BPM) motor - circulator pumps. This measure applies to the installation of an ECM or BPM circulator pump for space heating or hot water applications.
[5 empty] | Energy Savings (kWh/yr) | Summer Peak Demand Savings (kW) | Winter Peak Demand Savings (kW)
[5 empty] | 0 | 0 | 0
Date
Project Site
Building Type
Total Cost
| Project Type | Project Type | Pump Application | Pump Quantity | Baseline Pump Motor Horsepower (hp) | Baseline Pump Control | ECM Horsepower (hp) | ECM Pump Control | Equipment Cost
1
2
3
4
5
6
7
8
9
10
Maryland TRM V11 - p. 91

## Data Export (hidden)
DSMT API Name |  | AHRI_Number__c | Annual_Electric_Energy_Savings_kwh__c | Approved_On__c | Installation_Type__c | Make__c | Created_Date__c | EFLH_Cooling__c | Annual_Operating_Hours_hours_year__c | ARI_Type__c | Baseline_CEER__c | Baseline_COP__c | Baseline_EER__c | Baseline_HSPF__c | Baseline_IEER__c | Baseline_IPLV__c | Baseline_Motor_Efficiency__c | Baseline_Motor_Horsepower_hp__c | Baseline_Motor_Load_Factor__c | Baseline_SEER__c | Chiller_Operating_Condition__c | Chiller_Type__c | Coincidence_Factor__c | Compressor_Control_Type__c | Connected_to_Network__c | Cooling_BTUH__c | Cooling_Capacity_tons__c | Efficient_CEER__c | Equipment_Cost__c | Efficient_Coefficient_of_Performance__c | Efficient_Energy_Efficiency_Ratio__c | Efficient_Flow_Control_Type__c | Efficient_Heat_Seasonal_Prfrmnce_Factor__c | Efficient_IEER__c | Efficient_IPLV__c | ENERGY_STAR_Certified__c | Efficient_Motor_Efficiency__c | Efficient_Seasonal_Energy_Ratio__c | Existing_Heating_System_Type__c | EFLH_Cooling__c | EFLH_Heating__c | Factor_1__c | Factor_2__c | Factor_3__c | Energy_Savings_Factor__c | Factor_4__c | Existing_Cooling_System_Type__c | Existing_COP__c | Existing_EER__c | Existing_Equipment_Age_years__c | Existing_Flow_Control_Type__c | Existing_Heat_Seasonal_Prfrmnce_Factor__c | Existing_IEER__c | Existing_IPLV__c | Existing_Seasonal_Energy_Ratio__c | Geothermal_Heat_Pump_Type__c | Heating_BTUH__c | Heating_Section_Type__c | Height_in__c | High_Efficiency_Pump_HP__c | HVAC_Application__c | Indoor_Unit_Make__c | Indoor_Unit_Model__c | Invoice_Number__c | Measure_Description__c | Maximum_Design_Efficiency_kW_ton__c | Nominal_Cooling_Capacity_tons__c | Outdoor_Unit_Make__c | Outdoor_Unit_Model__c | Net_to_Gross__c | Payment_Batch__c | Remaining_Useful_Life_years__c | Room_Air_Conditioner_Type__c | Summer_Coincident_Peak_Demand_Savings_kW__c | Width_in__c | Existing_Thermostat_Type__c | CLR_CNI_Building_Type__c | Measure_Name_Text__c | Model__c | OrderLineId__c | Quantity__c | Project_End_Date_EA__c | SampleId__c | Total_Incentive_Cap_c | Total_Incentive_c | Existing_Heating_System_Type__c | Existing_Cooling_System_Type__c | Heating_BTUH__c | EFLH_Cooling__c | EFLH_Heating__c | Cooling_ESF__c | Heating_ESF__c | Baseline_SEER__c | Baseline_COP__c | Factor_1__c | Factor_2__c | Deemed_Annual_Energy_Savings_MMBtu__c | Deemed_Annual_Energy_Savings_Therms__c | AFUE__c | Fuel_Heat_Savings_%__c | Existing_Energy_Factor__c | Child__WC_Peak_Demand_Savings_kW__c | Factor_5__c | [8 empty] | Baseline_Average_Annual_Hours_of_Use__c |  | Efficient_Motor_Horsepower_hp_number__c | Type__c | Building_Type__c
Line Item | Measure Name | AHRI Number | Annual Electric Energy Savings (kWh) | Approved On | Installation Type | Make/Manufacturer | Created Date | Annual Operating Hours (hours/year) | Annual Operating Hours (hours/year) | ARI Type | Baseline CEER | Baseline COP | Baseline EER | Baseline HSPF | Baseline IEER | Baseline IPLV | Baseline Motor Efficiency (%) | Baseline Motor Horsepower (hp) | Baseline Motor Load Factor (%) | Baseline SEER | Chiller Operating Condition | Chiller Type | Coincidence Factor | Compressor Control Type | Connected to Network | Cooling Capacity (Btu/hr) | Cooling Capacity (tons) | Efficient CEER | Equipment Cost ($) If EA.Program_Name__c = Instant HVAC Discounts or Instant Lighting Discounts, then Retail Price (from import template) * Quantity | Efficient COP | Efficient EER | Efficient Flow Control Type | Efficient HSPF | Efficient IEER | Efficient IPLV | ENERGY STAR Certified | Efficient Motor Efficiency (%) | Efficient SEER | Existing Heating System Type | EFLH Cooling | EFLH Heating | Factor 1 | Factor 2 | Factor 3 | ETDF Summer | Factor 4 | Existing Cooling System Type | Existing COP | Existing EER | Existing Equipment Age (years) | Existing Flow Control Type | Existing HSPF | Existing IEER | Existing IPLV | Existing SEER | Geothermal Heat Pump Type | Heating Capacity (Btu/hr) | Heating Section Type | Height (in) | Horsepower of Pump Motor | HVAC Application | Indoor Unit Make | Indoor Unit Model Number | Invoice Number | Measure Description | Maximum Design Efficiency (kW/ton) | Nominal Cooling Capacity (tons) | Outdoor Unit Make | Outdoor Unit Model Number | Net to Gross | Payment Batch | Remaining Useful Life (years) | Room Air Conditioner Type | SC Peak Demand Savings (kW) | Width (in) | Existing Thermostat Type | Building Type | Measure Name Text | Model | OrderLineId | Quantity | Project End Date (EA) If EA.Program_Name__c = Instant HVAC Discounts or Instant Lighting Discounts, then EA.Purchase_Date__c | SampleId | Total Incentive Cap | Total Incentive | Existing Heating System Type | Existing Cooling System Type | Heating Capacity (Btu/hr) | EFLH Cooling | EFLH Heating | Cooling ESF | Heating ESF | Baseline SEER | Baseline COP | Factor 1 | Factor 2 | Deemed Annual Energy Savings | Deemed Annual Energy Savings (Therms) | AFUE | Fuel Heat Savings% | ETDF Winter | WC Peak Demand Savings (kW) |  | kWh cool | kWh heat | kWh vent | WATTS base | WATTS ee | IF kWh | HOURS vent | R | HOU DHW-base | η ee | Efficient Motor Horsepower (hp) | Type | Building Type
Note on CP2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Baseline SEER, COP, Factor 1 and Factor 2 - no longer relevant fields. Not used in calculation

## HVAC Lookups (hidden)
[12 empty] | Equipment | Type | Subcategory | Size Category | Options | Index Name | EER Base | IEER/SEER base | Qualifying EER | Qualifying IEER/SEER | Baseline Source
| ReplacementType |  | WaterCooledChiller |  | Space/Building Type | M-A TRM Mapped Building Type | EFLHcool | EFLHheat | EFLHgas | M-A TRM | Dual Enthalpy Savings Factor | [16 empty] | Measure | End Use | ISR | ISR last updated | ISR Lockdown | Notes
| Early Replacement |  | Centrifugal |  |  |  | Hagerstown, MD | Hagerstown, MD | Hagerstown, MD | Mapped | Hagerstown, MD | Air Conditioners | Air Cooled | Split | <5.4 tons | Electric Resistance (or None) | Air Cooled Split <5.4 tons Electric Resistance (or None) | 11.4168 | 13.4 | 11.4168 | 13.4 | IECC 2018 - Table C403.3.2(1) | [5 empty] | AC Tune-Up | HVAC | 1 | 2022 | No | ISR included as part of program-level realization rate, evaluated annually.
| New Construction |  | Centrifugal with VFD |  | Arena/Auditorium/Convention | Assembly | 849 | 1090 | 1755 | Assembly | 25 |  | Air Cooled | Split | <5.4 tons | Other | Air Cooled Split <5.4 tons Other | 11.4168 | 13.4 | 11.4168 | 13.4 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Advanced Rooftop Controls | HVAC | 1 | 2022 | No | ISR included as part of program-level realization rate, evaluated annually.
|  |  | Screw/Scroll |  | Auto-Related | Retail - Small | 828 | 608 | 545 | Small Retail | 56 |  | Air Cooled | Packaged | <5.4 tons | Electric Resistance (or None) | Air Cooled Packaged <5.4 tons Electric Resistance (or None) | 11.4168 | 13.4 | 11.4168 | 13.4 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Boiler Reset and Cut-Out Controls | HVAC | 1 | 2022 | No | ISR included as part of program-level realization rate, evaluated annually.
|  |  | Reciprocating |  | Convenience Stores | Grocery | 610 | 962 | 962 | Small Retail | 56 |  | Air Cooled | Packaged | <5.4 tons | Other | Air Cooled Packaged <5.4 tons Other | 11.4168 | 13.4 | 11.4168 | 13.4 | IECC 2018 - Table C403.3.2(1) | [5 empty] | C&I Draft Unitary Code Change IMP | HVAC | 1 | 2022 | No | ISR included as part of program-level realization rate, evaluated annually.
| EfficiencyUnits |  | Screw/Scroll/Reciprocating with VFD |  | Daycare | Education - Primary School | 265 | 653 | 510 | Primary School | 39 |  | Air Cooled | Split | ≥5.4 to <11.25 tons | Electric Resistance (or None) | Air Cooled Split ≥5.4 to <11.25 tons Electric Resistance (or None) | 11.2 | 14.8 | 11.76 | 15.54 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Commercial Gas Boiler | HVAC | 1 | 2022 | No | ISR included as part of program-level realization rate, evaluated annually.
| EER/SEER/IEER |  |  |  | Education – College/University | Education - University | 713 | 518 | 947 | Other | 56 |  | Air Cooled | Split | ≥5.4 to <11.25 tons | Other | Air Cooled Split ≥5.4 to <11.25 tons Other | 11.2 | 14.8 | 11.76 | 15.54 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Commercial Gas Furnace <255,000 BTU/h | HVAC | 1 | 2022 | No | ISR included as part of program-level realization rate, evaluated annually.
| kW/ton |  | AirCooledChiller |  | Education – K-12 | Education - Secondary School | 305 | 703 | 615 | Primary School | 39 |  | Air Cooled | Packaged | ≥5.4 to <11.25 tons | Electric Resistance (or None) | Air Cooled Packaged ≥5.4 to <11.25 tons Electric Resistance (or None) | 11.2 | 14.8 | 11.76 | 15.54 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Commercial Gas Furnace ≥225,000 BTU/h | HVAC | 1 | 2022 | No | ISR included as part of program-level realization rate, evaluated annually.
|  |  | Centrifugal |  | Grocery | Grocery | 610 | 962 | 962 | Small Retail | 56 |  | Air Cooled | Packaged | ≥5.4 to <11.25 tons | Other | Air Cooled Packaged ≥5.4 to <11.25 tons Other | 11.2 | 14.8 | 11.76 | 15.54 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Demand Controlled Ventilation/ DCV | HVAC | 1 | 2022 | No | ISR included as part of program-level realization rate, evaluated annually.
| CapacityUnits |  | Centrifugal with VFD |  | Gymnasium/Performing Arts Theater | Assembly | 849 | 1090 | 1755 | Assembly | 25 |  | Air Cooled | Split | ≥11.25 to <20 tons | Electric Resistance (or None) | Air Cooled Split ≥11.25 to <20 tons Electric Resistance (or None) | 11 | 14.2 | 11.55 | 14.91 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Dual Enthalpy Economizer | HVAC | 1 | 2022 | No | ISR included as part of program-level realization rate, evaluated annually.
| tons |  | Screw/Scroll/Reciprocating |  | Industrial – 1 Shift/Light Mfctg | Manufacturing - 1 shift/Lighting Industrial | 413 | 572 | 709 | Light Industrial | 23 |  | Air Cooled | Split | ≥11.25 to <20 tons | Other | Air Cooled Split ≥11.25 to <20 tons Other | 11 | 14.2 | 11.55 | 14.91 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Ductless Mini-Split Heat Pump (DMSHP) | HVAC | 1 | 2022 | No | ISR included as part of program-level realization rate, evaluated annually.
| Btu/h |  |  |  | Industrial - 2 Shift | Manufacturing - Bio Tech/High Tech | 785 | 143 | 143 | Light Industrial | 23 |  | Air Cooled | Packaged | ≥11.25 to <20 tons | Electric Resistance (or None) | Air Cooled Packaged ≥11.25 to <20 tons Electric Resistance (or None) | 11 | 14.2 | 11.55 | 14.91 | IECC 2018 - Table C403.3.2(1) | [5 empty] | ECM Circulating Fan | HVAC | 1 | 2022 | No | ISR included as part of program-level realization rate, evaluated annually.
|  |  | RoomAirConditioner |  | Industrial - 3 Shift | Manufacturing - Bio Tech/High Tech | 785 | 143 | 143 | Light Industrial | 23 |  | Air Cooled | Packaged | ≥11.25 to <20 tons | Other | Air Cooled Packaged ≥11.25 to <20 tons Other | 11 | 14.2 | 11.55 | 14.91 | IECC 2018 - Table C403.3.2(1) | [5 empty] | ECM Circulator Pump | HVAC | 1 | 2022 | No | ISR included as part of program-level realization rate, evaluated annually.
| AirCooledChillerTier |  | Without Reverse Cycle With louvered sides |  | Lodging - Common Areas | Multi-Family (Common Areas) | 1367 | 250 | 1488 | Other | 56 |  | Air Cooled | Split | ≥20 to <63.3 tons | Electric Resistance (or None) | Air Cooled Split ≥20 to <63.3 tons Electric Resistance (or None) | 10 | 13.2 | 10.5 | 13.86 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Electric Chillers | HVAC | 1 | 2022 | No | ISR included as part of program-level realization rate, evaluated annually.
| Path A |  | Without Reverse Cycle Without louvered sides |  | Lodging (MF, Dorms) | Lodging - Hotel | 1645 | 2193 | 1239 | Other | 56 |  | Air Cooled | Split | ≥20 to <63.3 tons | Other | Air Cooled Split ≥20 to <63.3 tons Other | 10 | 13.2 | 10.5 | 13.86 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Hotel Guest Room Occupancy Sensors - HVAC | HVAC | 1 | 2022 | No | ISR included as part of program-level realization rate, evaluated annually.
| Path B |  | With Reverse Cycle With louvered sides |  | Lodging Hotel (Guest Rooms) | Lodging - Hotel | 1645 | 2193 | 1239 | Other | 56 |  | Air Cooled | Packaged | ≥20 to <63.3 tons | Electric Resistance (or None) | Air Cooled Packaged ≥20 to <63.3 tons Electric Resistance (or None) | 10 | 13.2 | 10.5 | 13.86 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Infrared Heaters | HVAC | 1 | 2022 | No | ISR included as part of program-level realization rate, evaluated annually.
|  |  | With Reverse Cycle Without louvered sides |  | Medical - Clinic | Office - Small | 569 | 430 | 419 | Small Office | 56 |  | Air Cooled | Packaged | ≥20 to <63.3 tons | Other | Air Cooled Packaged ≥20 to <63.3 tons Other | 10 | 13.2 | 10.5 | 13.86 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Low-E Film - Electric | HVAC | 1 | 2022 | No | ISR included as part of program-level realization rate, evaluated annually.
| WaterCooledChillerTier |  | Casement Only |  | Medical - Hospital | Health/Medical - Hospital | 1099 | 209 | 302 | Other | 56 |  | Air Cooled | Split | ≥63.3 tons | Electric Resistance (or None) | Air Cooled Split ≥63.3 tons Electric Resistance (or None) | 9.7 | 12.5 | 10.185 | 13.125 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Smart Thermostat* | HVAC | 1 | 2022 | No | ISR included as part of program-level realization rate, evaluated annually.
| Path A |  | Casement Slider |  | Multifamily/Common Areas | Multi-Family (Common Areas) | 1367 | 250 | 1488 | Other | 56 |  | Air Cooled | Split | ≥63.3 tons | Other | Air Cooled Split ≥63.3 tons Other | 9.7 | 12.5 | 10.185 | 13.125 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Steam Boiler Traps – Repair/Replace | HVAC | 1 | 2022 | No | ISR included as part of program-level realization rate, evaluated annually.
| Path B |  |  |  | Museum/Library | Office - Small | 569 | 430 | 419 | Small Office | 56 |  | Air Cooled | Packaged | ≥63.3 tons | Electric Resistance (or None) | Air Cooled Packaged ≥63.3 tons Electric Resistance (or None) | 9.7 | 12.5 | 10.185 | 13.125 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Switch Reluctance Motors | HVAC | 1 | 2022 | No | ISR included as part of program-level realization rate, evaluated annually.
|  |  | PackagedTerminalAirConditioner |  | Nursing Homes | Health/Medical - Nursing Home | 584 | 912 | 1433 | Other | 56 |  | Air Cooled | Packaged | ≥63.3 tons | Other | Air Cooled Packaged ≥63.3 tons Other | 9.7 | 12.5 | 10.185 | 13.125 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Tune-Up Chiller System | HVAC | 1 | 2022 | No | ISR included as part of program-level realization rate, evaluated annually.
| GeothermalHeatPumpTier |  | Standard Size |  | Office | Office - Small | 569 | 430 | 419 | Small Office | 56 |  | Water Cooled | Split | <5.4 tons | Electric Resistance (or None) | Water Cooled Split <5.4 tons Electric Resistance (or None) | 12.1 | 12.3 | 12.1 | 12.3 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Unitary HVAC Systems | HVAC | 1 | 2022 | No | ISR included as part of program-level realization rate, evaluated annually.
| Tier 1 |  | Non Standard Size |  | Other | Office - Small | 569 | 430 | 419 | Other | 56 |  | Water Cooled | Split | <5.4 tons | Other | Water Cooled Split <5.4 tons Other | 12.1 | 12.3 | 12.1 | 12.3 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Variable Frequency Drive (VFD) for HVAC | HVAC | 1 | 2022 | No | ISR included as part of program-level realization rate, evaluated annually.
| Tier 2 |  |  |  | Penitentiary | Health/Medical - Hospital | 1099 | 209 | 302 | Other | 56 |  | Water Cooled | Packaged | <5.4 tons | Electric Resistance (or None) | Water Cooled Packaged <5.4 tons Electric Resistance (or None) | 12.1 | 12.3 | 12.1 | 12.3 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Variable Refrigerant Flow (VRF) Heat Pump Systems | HVAC | 1 | 2022 | No | ISR included as part of program-level realization rate, evaluated annually.
|  |  | PackagedTerminalHeatPump |  | Police/Fire Stations | Office - Small | 569 | 430 | 419 | Small Office | 56 |  | Water Cooled | Packaged | <5.4 tons | Other | Water Cooled Packaged <5.4 tons Other | 12.1 | 12.3 | 12.1 | 12.3 | IECC 2018 - Table C403.3.2(1) | [5 empty] | https://docs.google.com/spreadsheets/d/1cGQPjPu2UuWpvB6MXTCUMPFJOqbGMYsd/edit#gid=874354190
| Economizer Control |  | Standard Size |  | Post Office/Town Hall/Court | Office - Small | 569 | 430 | 419 | Small Office | 56 |  | Water Cooled | Split | ≥5.4 to <11.25 tons | Electric Resistance (or None) | Water Cooled Split ≥5.4 to <11.25 tons Electric Resistance (or None) | 12.1 | 13.9 | 12.705 | 14.595 | IECC 2018 - Table C403.3.2(1)
| None |  | Non-Standard Size |  | Public Assembly | Assembly | 849 | 1090 | 1755 | Assembly | 25 |  | Water Cooled | Split | ≥5.4 to <11.25 tons | Other | Water Cooled Split ≥5.4 to <11.25 tons Other | 12.1 | 13.9 | 12.705 | 14.595 | IECC 2018 - Table C403.3.2(1)
| Dual Enthalpy Economizer |  |  |  | Public Order/Safety | Office - Small | 569 | 430 | 419 | Small Office | 56 |  | Water Cooled | Packaged | ≥5.4 to <11.25 tons | Electric Resistance (or None) | Water Cooled Packaged ≥5.4 to <11.25 tons Electric Resistance (or None) | 12.1 | 13.9 | 12.705 | 14.595 | IECC 2018 - Table C403.3.2(1) | [5 empty] | load_shape_name | Building Type | ETDF_summer peak | ETDF_winter peak |  | Space/Building Type for HVAC units | ETDF Mapped Bldg Type
| Other |  | GeothermalHeatPump |  | Public Services (Non-food) | Office - Small | 569 | 430 | 419 | Small Office | 56 |  | Water Cooled | Packaged | ≥5.4 to <11.25 tons | Other | Water Cooled Packaged ≥5.4 to <11.25 tons Other | 12.1 | 13.9 | 12.705 | 14.595 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Cooling | FullServiceRestaurant | 0.0008328 | -
|  |  | Water Source Heat Pump |  | Religious Worship/Church | Office - Small | 569 | 430 | 419 | Religious | 6 |  | Water Cooled | Split | ≥11.25 to <20 tons | Electric Resistance (or None) | Water Cooled Split ≥11.25 to <20 tons Electric Resistance (or None) | 12.5 | 13.9 | 13.125 | 14.595 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Cooling | Hospital | 0.0003778 | - |  | Arena/Auditorium/Convention | Other
| Air Conditioner Types |  | Ground Water Source Heat Pump |  | Restaurant - Fast-Food | Restaurant - Fast-Food | 656 | 1199 | 798 | Fast Food | 36 |  | Water Cooled | Split | ≥11.25 to <20 tons | Other | Water Cooled Split ≥11.25 to <20 tons Other | 12.5 | 13.9 | 13.125 | 14.595 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Cooling | LargeHotel | 0.0004755 | - |  | Auto-Related | RetailStripmall
| Air Cooled |  | Ground Source Heat Pump |  | Restaurant - Sit-Down | Restaurant - Sit-Down | 690 | 1106 | 828 | Full Service Restaurant | 29 |  | Water Cooled | Packaged | ≥11.25 to <20 tons | Electric Resistance (or None) | Water Cooled Packaged ≥11.25 to <20 tons Electric Resistance (or None) | 12.5 | 13.9 | 13.125 | 14.595 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Cooling | LargeOffice | 0.0003938 | - |  | Convenience Stores | RetailStandalone
| Water Cooled |  |  |  | Retail - Large | Retail - Single-Story Large | 819 | 722 | 722 | Big Box Retail | 56 |  | Water Cooled | Packaged | ≥11.25 to <20 tons | Other | Water Cooled Packaged ≥11.25 to <20 tons Other | 12.5 | 13.9 | 13.125 | 14.595 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Cooling | MediumOffice | 0.0006711 | - |  | Daycare | PrimarySchool
| Evaporatively Cooled |  | UnitaryAirConditioner |  | Retail - Small | Retail - Small | 828 | 608 | 545 | Small Retail | 56 |  | Water Cooled | Split | ≥20 to <63.3 tons | Electric Resistance (or None) | Water Cooled Split ≥20 to <63.3 tons Electric Resistance (or None) | 12.4 | 13.6 | 13.02 | 14.28 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Cooling | Outpatient | 0.000601 | - |  | Education – College/University | SecondarySchool
|  |  | Split |  | Storage - Conditioned | Storage - Conditioned | 220 | 835 | 457 | Warehouse | 2 |  | Water Cooled | Split | ≥20 to <63.3 tons | Other | Water Cooled Split ≥20 to <63.3 tons Other | 12.4 | 13.6 | 13.02 | 14.28 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Cooling | PrimarySchool | 0.0010188 | - |  | Education – K-12 | SecondarySchool
| Heat Pump Types |  | Packaged |  | Storage - Unconditioned |  | 0 | 0 | 0 | Other | 56 |  | Water Cooled | Packaged | ≥20 to <63.3 tons | Electric Resistance (or None) | Water Cooled Packaged ≥20 to <63.3 tons Electric Resistance (or None) | 12.4 | 13.6 | 13.02 | 14.28 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Cooling | QuickServiceRestaurant | 0.0007826 | - |  | Grocery | RetailStandalone
| Air Source |  |  |  | Warehouses (Not Refrigerated) | Storage - Conditioned | 220 | 835 | 457 | Warehouse | 2 |  | Water Cooled | Packaged | ≥20 to <63.3 tons | Other | Water Cooled Packaged ≥20 to <63.3 tons Other | 12.4 | 13.6 | 13.02 | 14.28 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Cooling | RetailStandalone | 0.0008876 | - |  | Gymnasium/Performing Arts Theater | Other
| Water Source |  | UnitaryHeatPump |  | Warehouses (Refrigerated) | Warehouse - Refrigerated | 3520 | 335 | 335 | Other | 56 |  | Water Cooled | Split | ≥63.3 tons | Electric Resistance (or None) | Water Cooled Split ≥63.3 tons Electric Resistance (or None) | 12.2 | 13.5 | 12.81 | 14.175 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Cooling | RetailStripmall | 0.0008139 | - |  | Industrial – 1 Shift/Light Mfctg | Warehouse
| Ground Source |  | Split |  | Waste Water Treatment Plant | Office - Small | 569 | 430 | 419 | Small Office | 56 |  | Water Cooled | Split | ≥63.3 tons | Other | Water Cooled Split ≥63.3 tons Other | 12.2 | 13.5 | 12.81 | 14.175 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Cooling | SecondarySchool | 0.0008522 | - |  | Industrial - 2 Shift | Warehouse
|  |  | Packaged |  |  | Maryland TRM V11 Appendix D |  |  |  | Maryland TRM V11 - p.85 |  |  | Water Cooled | Packaged | ≥63.3 tons | Electric Resistance (or None) | Water Cooled Packaged ≥63.3 tons Electric Resistance (or None) | 12.2 | 13.5 | 12.81 | 14.175 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Cooling | SmallHotel | 0.000655 | - |  | Industrial - 3 Shift | Warehouse
| Air Source Types | [11 empty] | Water Cooled | Packaged | ≥63.3 tons | Other | Water Cooled Packaged ≥63.3 tons Other | 12.2 | 13.5 | 12.81 | 14.175 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Cooling | SmallOffice | 0.0010049 | - |  | Lodging - Common Areas | LargeHotel
| Split |  | VRFHeatPump | [9 empty] | Evaporatively Cooled | Split | <5.4 tons | Electric Resistance (or None) | Evaporatively Cooled Split <5.4 tons Electric Resistance (or None) | 12.1 | 12.3 | 12.1 | 12.3 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Cooling | Warehouse | 0.0015434 | - |  | Lodging (MF, Dorms) | LargeHotel
| Packaged |  | with Heat Recovery |  | Equipment | Measure Life |  | Conversion Factors |  |  |  |  | Evaporatively Cooled | Split | <5.4 tons | Other | Evaporatively Cooled Split <5.4 tons Other | 12.1 | 12.3 | 12.1 | 12.3 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Cooling | Other | 0.000692 | - |  | Lodging Hotel (Guest Rooms) | LargeHotel
|  |  | without Heat Recovery |  | Chillers | 23 |  | Type | SEER2 | EER2 | HSPF2 |  | Evaporatively Cooled | Packaged | <5.4 tons | Electric Resistance (or None) | Evaporatively Cooled Packaged <5.4 tons Electric Resistance (or None) | 12.1 | 12.3 | 12.1 | 12.3 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Electric Heat | FullServiceRestaurant | - | 0.0008317 |  | Medical - Clinic | Outpatient
| Water Source Types |  |  |  | Air Conditioners | 15 |  | Ducted | 0.95 | 0.95 | 0.85 |  | Evaporatively Cooled | Packaged | <5.4 tons | Other | Evaporatively Cooled Packaged <5.4 tons Other | 12.1 | 12.3 | 12.1 | 12.3 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Electric Heat | Hospital | - | 0.001547 |  | Medical - Hospital | Hospital
| Water to Air |  | HeatingType |  | Air Source Heat Pumps | 15 |  | Non-Ducted | 1 | 1 | 0.9 |  | Evaporatively Cooled | Split | ≥5.4 to <11.25 tons | Electric Resistance (or None) | Evaporatively Cooled Split ≥5.4 to <11.25 tons Electric Resistance (or None) | 12.1 | 12.3 | 12.705 | 12.915 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Electric Heat | LargeHotel | - | 0.0010263 |  | Multifamily/Common Areas | Other
| Water to Water |  | Electric Resistance |  | PTAC/PTHP | 15 |  | Packaged | 0.95 | 0.95 | 0.84 |  | Evaporatively Cooled | Split | ≥5.4 to <11.25 tons | Other | Evaporatively Cooled Split ≥5.4 to <11.25 tons Other | 12.1 | 12.3 | 12.705 | 12.915 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Electric Heat | LargeOffice | - | 0.0010677 |  | Museum/Library | SmallOffice
|  |  | Other |  | DMSHP | 15 | [6 empty] | Evaporatively Cooled | Packaged | ≥5.4 to <11.25 tons | Electric Resistance (or None) | Evaporatively Cooled Packaged ≥5.4 to <11.25 tons Electric Resistance (or None) | 12.1 | 12.3 | 12.705 | 12.915 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Electric Heat | MediumOffice | - | 0.0013316 |  | Nursing Homes | Hospital
| Ground Source Types |  | None |  | VFD | 15 | [6 empty] | Evaporatively Cooled | Packaged | ≥5.4 to <11.25 tons | Other | Evaporatively Cooled Packaged ≥5.4 to <11.25 tons Other | 12.1 | 12.3 | 12.705 | 12.915 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Electric Heat | Outpatient | - | 0.0013069 |  | Office | SmallOffice
| Brine to Air |  |  |  | Dual Enthalpy Economizer | 7 |  | Type | CF PJM | CF Upeak/SSP |  |  | Evaporatively Cooled | Split | ≥11.25 to <20 tons | Electric Resistance (or None) | Evaporatively Cooled Split ≥11.25 to <20 tons Electric Resistance (or None) | 12 | 12.2 | 12.6 | 12.81 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Electric Heat | PrimarySchool | - | 0.0012313 |  | Other | Other
| Brine to Water |  | Chillers |  | Smart Thermostat | 7.5 |  | GSHP/WSHP | 0.66 | 0.69 |  |  | Evaporatively Cooled | Split | ≥11.25 to <20 tons | Other | Evaporatively Cooled Split ≥11.25 to <20 tons Other | 12 | 12.2 | 12.6 | 12.81 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Electric Heat | QuickServiceRestaurant | - | 0.0007381 |  | Penitentiary | Other
| Groundwater Source Types |  | Air Cooled |  | Room Air Conditioner | 9 | [6 empty] | Evaporatively Cooled | Packaged | ≥11.25 to <20 tons | Electric Resistance (or None) | Evaporatively Cooled Packaged ≥11.25 to <20 tons Electric Resistance (or None) | 12 | 12.2 | 12.6 | 12.81 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Electric Heat | RetailStandalone | - | 0.0010828 |  | Police/Fire Stations | SmallOffice
| Water to Air |  | Water Cooled, Positive Displacement |  | GSHP | 15 |  | Mid-Atlantic TRM V10 |  |  |  |  | Evaporatively Cooled | Packaged | ≥11.25 to <20 tons | Other | Evaporatively Cooled Packaged ≥11.25 to <20 tons Other | 12 | 12.2 | 12.6 | 12.81 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Electric Heat | RetailStripmall | - | 0.00111 |  | Post Office/Town Hall/Court | SmallOffice
| Water to Water |  | Water Cooled, Centrifugal |  | WSHP | 15 | [6 empty] | Evaporatively Cooled | Split | ≥20 to <63.3 tons | Electric Resistance (or None) | Evaporatively Cooled Split ≥20 to <63.3 tons Electric Resistance (or None) | 11.9 | 12.1 | 12.495 | 12.705 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Electric Heat | SecondarySchool | - | 0.0009643 |  | Public Assembly | Other
[5 empty] | Circulating Fan | 5 | [6 empty] | Evaporatively Cooled | Split | ≥20 to <63.3 tons | Other | Evaporatively Cooled Split ≥20 to <63.3 tons Other | 11.9 | 12.1 | 12.495 | 12.705 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Electric Heat | SmallHotel | - | 0.0009789 |  | Public Order/Safety | SmallOffice
| PTAC/PTHP Types |  | Mini-Splits |  | Circulator Pump | 15 | [6 empty] | Evaporatively Cooled | Packaged | ≥20 to <63.3 tons | Electric Resistance (or None) | Evaporatively Cooled Packaged ≥20 to <63.3 tons Electric Resistance (or None) | 11.9 | 12.1 | 12.495 | 12.705 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Electric Heat | SmallOffice | - | 0.0012355 |  | Public Services (Non-food) | SmallOffice
| New Construction - Standard Size |  | Ductless Mini-Split Air Conditioner |  | Chiller Tune Up | 3 | [6 empty] | Evaporatively Cooled | Packaged | ≥20 to <63.3 tons | Other | Evaporatively Cooled Packaged ≥20 to <63.3 tons Other | 11.9 | 12.1 | 12.495 | 12.705 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Electric Heat | Warehouse | - | 0.0017429 |  | Religious Worship/Church | SmallOffice
| Early Replacement - Non-Standard Size |  | Ductless Mini-Split Heat Pump |  | Switch Reluctance Motor | 12 | [6 empty] | Evaporatively Cooled | Split | ≥63.3 tons | Electric Resistance (or None) | Evaporatively Cooled Split ≥63.3 tons Electric Resistance (or None) | 11.7 | 11.9 | 12.285 | 12.495 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Electric Heat | Other | - | 0.0011055 |  | Restaurant - Fast-Food | QuickServiceRestaurant
[5 empty] | Hotel Room Occ Sensor | 15 | [6 empty] | Evaporatively Cooled | Split | ≥63.3 tons | Other | Evaporatively Cooled Split ≥63.3 tons Other | 11.7 | 11.9 | 12.285 | 12.495 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Heat Recovery | FullServiceRestaurant | 0.0001353 | 0.0001216 |  | Restaurant - Sit-Down | FullServiceRestaurant
| Water Heater Type |  | PTAC/PTHP |  | Low-e Film | 10 | [6 empty] | Evaporatively Cooled | Packaged | ≥63.3 tons | Electric Resistance (or None) | Evaporatively Cooled Packaged ≥63.3 tons Electric Resistance (or None) | 11.7 | 11.9 | 12.285 | 12.495 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Heat Recovery | Hospital | 0.0001154 | 0.0001093 |  | Retail - Large | RetailStandalone
| Electric w/ Desuperheater |  | Packaged Terminal Air Conditioner |  | VRF Heat Pump | 15 | [6 empty] | Evaporatively Cooled | Packaged | ≥63.3 tons | Other | Evaporatively Cooled Packaged ≥63.3 tons Other | 11.7 | 11.9 | 12.285 | 12.495 | IECC 2018 - Table C403.3.2(1) | [5 empty] | Heat Recovery | LargeHotel | 0.0001554 | 0.0001336 |  | Retail - Small | RetailStripmall
| Electric - no Desuperheater |  | Packaged Terminal Heat Pump | [9 empty] | Type | Subcategory | Size Category | Options | Index Name | CEER Base | Qualifying CEER |  |  | Baseline Source | [5 empty] | Heat Recovery | LargeOffice | 0.0001139 | 0.00014 |  | Storage - Conditioned | Warehouse
| Gas | [26 empty] | Heat Recovery | MediumOffice | 0.0001293 | 0.0001337 |  | Storage - Unconditioned | Other
| Other |  | Connected to Network | [9 empty] | Room Air Conditioner | Without Reverse Cycle | <8,000 Btu/h | With Louvered Sides | Room Air Conditioner Without Reverse Cycle <8,000 Btu/h With Louvered Sides | 11 | 12.1 |  |  | IECC 2018 - Table C403.3.2(3) | [5 empty] | Heat Recovery | Outpatient | 0.000155 | 0.0001337 |  | Warehouses (Not Refrigerated) | Warehouse
|  |  | No | [9 empty] | Room Air Conditioner | Without Reverse Cycle | ≥8,000 to ≤10,999 Btu/h | With Louvered Sides | Room Air Conditioner Without Reverse Cycle ≥8,000 to ≤10,999 Btu/h With Louvered Sides | 10.9 | 12 |  |  | IECC 2018 - Table C403.3.2(3) | [5 empty] | Heat Recovery | PrimarySchool | 0.0001659 | 0.0001618 |  | Warehouses (Refrigerated) | Warehouse
| Room AC |  | Yes | [9 empty] | Room Air Conditioner | Without Reverse Cycle | ≥11,000 to ≤13,999 Btu/h | With Louvered Sides | Room Air Conditioner Without Reverse Cycle ≥11,000 to ≤13,999 Btu/h With Louvered Sides | 10.9 | 12 |  |  | IECC 2018 - Table C403.3.2(3) | [5 empty] | Heat Recovery | QuickServiceRestaurant | 0.0001428 | 0.0001343 |  | Waste Water Treatment Plant | Other
| Without Reverse Cycle | [11 empty] | Room Air Conditioner | Without Reverse Cycle | ≥14,000 to ≤19,999 Btu/h | With Louvered Sides | Room Air Conditioner Without Reverse Cycle ≥14,000 to ≤19,999 Btu/h With Louvered Sides | 10.7 | 11.8 |  |  | IECC 2018 - Table C403.3.2(3) | [5 empty] | Heat Recovery | RetailStandalone | 0.0001467 | 0.0001306
| With Reverse Cycle |  | GSHP WSHP Type | [9 empty] | Room Air Conditioner | Without Reverse Cycle | ≥20,000 to ≤24,999 Btu/h | With Louvered Sides | Room Air Conditioner Without Reverse Cycle ≥20,000 to ≤24,999 Btu/h With Louvered Sides | 9.4 | 10.3 |  |  | IECC 2018 - Table C403.3.2(3) | [5 empty] | Heat Recovery | RetailStripmall | 0.0001638 | 0.0001219
| Casement Only |  | Water Source | [9 empty] | Room Air Conditioner | Without Reverse Cycle | ≥25,000 to ≤27,999 Btu/h | With Louvered Sides | Room Air Conditioner Without Reverse Cycle ≥25,000 to ≤27,999 Btu/h With Louvered Sides | 9.4 | 10.3 |  |  | IECC 2018 - Table C403.3.2(3) | [5 empty] | Heat Recovery | SecondarySchool | 0.0001525 | 0.000167
| Casement-Slider |  | Ground Source | [9 empty] | Room Air Conditioner | Without Reverse Cycle | ≥28,000 Btu/h | With Louvered Sides | Room Air Conditioner Without Reverse Cycle ≥28,000 Btu/h With Louvered Sides | 9 | 9.9 |  |  | IECC 2018 - Table C403.3.2(3) | [5 empty] | Heat Recovery | SmallHotel | 0.0001106 | 0.0001327
| With Louvered Sides |  | Groundwater Source | [9 empty] | Room Air Conditioner | Without Reverse Cycle | <8,000 Btu/h | Without Louvered Sides | Room Air Conditioner Without Reverse Cycle <8,000 Btu/h Without Louvered Sides | 10 | 11 |  |  | IECC 2018 - Table C403.3.2(3) | [5 empty] | Heat Recovery | SmallOffice | 0.0001365 | 0.0001261
| Without Louvered Sides |  | Water_Source | [9 empty] | Room Air Conditioner | Without Reverse Cycle | ≥8,000 to ≤10,999 Btu/h | Without Louvered Sides | Room Air Conditioner Without Reverse Cycle ≥8,000 to ≤10,999 Btu/h Without Louvered Sides | 9.6 | 10.6 |  |  | IECC 2018 - Table C403.3.2(3) | [5 empty] | Heat Recovery | Warehouse | 0.000114 | 0.0001211
|  |  | Ground_Source | [9 empty] | Room Air Conditioner | Without Reverse Cycle | ≥11,000 to ≤13,999 Btu/h | Without Louvered Sides | Room Air Conditioner Without Reverse Cycle ≥11,000 to ≤13,999 Btu/h Without Louvered Sides | 9.5 | 10.5 |  |  | IECC 2018 - Table C403.3.2(3) | [5 empty] | Heat Recovery | Other | 0.0001365 | 0.000132
| Chiller Control Type |  | Groundwater_Source | [9 empty] | Room Air Conditioner | Without Reverse Cycle | ≥14,000 to ≤19,999 Btu/h | Without Louvered Sides | Room Air Conditioner Without Reverse Cycle ≥14,000 to ≤19,999 Btu/h Without Louvered Sides | 9.3 | 10.2 |  |  | IECC 2018 - Table C403.3.2(3) | [5 empty] | Heat Rejection | Hospital | 0.0002471 | 1.83e-05
| VFD | [11 empty] | Room Air Conditioner | Without Reverse Cycle | ≥20,000 to ≤24,999 Btu/h | Without Louvered Sides | Room Air Conditioner Without Reverse Cycle ≥20,000 to ≤24,999 Btu/h Without Louvered Sides | 9.4 | 10.3 |  |  | IECC 2018 - Table C403.3.2(3) | [5 empty] | Heat Rejection | LargeHotel | 0.0002835 | 1.64e-05
| Other | [11 empty] | Room Air Conditioner | Without Reverse Cycle | ≥25,000 to ≤27,999 Btu/h | Without Louvered Sides | Room Air Conditioner Without Reverse Cycle ≥25,000 to ≤27,999 Btu/h Without Louvered Sides | 9.4 | 10.3 |  |  | IECC 2018 - Table C403.3.2(3) | [5 empty] | Heat Rejection | LargeOffice | 0.0003122 | 2.3e-05
[13 empty] | Room Air Conditioner | Without Reverse Cycle | ≥28,000 Btu/h | Without Louvered Sides | Room Air Conditioner Without Reverse Cycle ≥28,000 Btu/h Without Louvered Sides | 9.4 | 10.3 |  |  | IECC 2018 - Table C403.3.2(3) | [5 empty] | Heat Rejection | MediumOffice | 0.0003341 | 1.62e-05
| Data Export Field Names | [11 empty] | Room Air Conditioner | With Reverse Cycle | <14,000 Btu/h | Without Louvered Sides | Room Air Conditioner With Reverse Cycle <14,000 Btu/h Without Louvered Sides | 9.3 | 10.2 |  |  | IECC 2018 - Table C403.3.2(3) | [5 empty] | Heat Rejection | Outpatient | 0.0003055 | 1.85e-05
| Central Air Conditioner < 5.4 tons - New construction or replacing non-functional equipment | [11 empty] | Room Air Conditioner | With Reverse Cycle | ≥14,000 Btu/h | Without Louvered Sides | Room Air Conditioner With Reverse Cycle ≥14,000 Btu/h Without Louvered Sides | 8.7 | 9.6 |  |  | IECC 2018 - Table C403.3.2(3) | [5 empty] | Heat Rejection | PrimarySchool | 0.0005103 | 1.58e-05
| Central Air Conditioner < 5.4 tons - Replacing functional equip < 15 yrs old | [11 empty] | Room Air Conditioner | With Reverse Cycle | <20,000 Btu/h | With Louvered Sides | Room Air Conditioner With Reverse Cycle <20,000 Btu/h With Louvered Sides | 9.8 | 10.8 |  |  | IECC 2018 - Table C403.3.2(3) | [5 empty] | Heat Rejection | RetailStripmall | 0.000586 | 7.6e-06
| Central Air Conditioner >= 5.4 tons - New Con or replace non-functional equip | [11 empty] | Room Air Conditioner | With Reverse Cycle | ≥20,000 Btu/h | With Louvered Sides | Room Air Conditioner With Reverse Cycle ≥20,000 Btu/h With Louvered Sides | 9.3 | 10.2 |  |  | IECC 2018 - Table C403.3.2(3) | [5 empty] | Heat Rejection | SecondarySchool | 0.0003975 | 8.7e-06
| Central Air Conditioner >= 5.4 tons - Replace functional equip < 15 yrs old | [11 empty] | Room Air Conditioner | Casement only | All sizes |  | Room Air Conditioner Casement only All sizes | 9.5 | 10.5 |  |  | IECC 2018 - Table C403.3.2(3) | [5 empty] | Heat Rejection | SmallOffice | 0.0005248 | 1.7e-06
| Water-Cooled and Evap Cooled Air Cond - New Con or replace non-functional | [11 empty] | Room Air Conditioner | Casement-Slider | All sizes |  | Room Air Conditioner Casement-Slider All sizes | 10.4 | 11.4 |  |  | IECC 2018 - Table C403.3.2(3) | [5 empty] | Heat Rejection | Warehouse | 0.0005679 | 1e-05
| Water-Cooled and Evap Cooled Air Cond - Replace functional equip < 15 yrs old | [26 empty] | Heat Rejection | Other | 0.0004074 | 1.57e-05
| Air Source Heat Pump < 5.4 tons - New Con or replace non-functional equipment | [26 empty] | Pumps | FullServiceRestaurant | 0.0001572 | 0.0001146
| Air Source Heat Pump < 5.4 tons - Replace functional equipment < 15 yrs old | [10 empty] | Equipment | Type | Subcategory | Size Category | Options | Index Name | EER/EER2 Base | SEER2 Base | HSPF2/COP Base | Qualifying EER | Qualifying IEER/SEER2 | Qualifying COP/HSPF2 | Tier 2 EER | Tier 2 COP | Baseline Source |  | Pumps | Hospital | 0.0001289 | 0.0001037
| Heat Pump - Cold Climate | [26 empty] | Pumps | LargeHotel | 0.0001273 | 0.0001138
[12 empty] | Heat Pumps | Air Source | Split | <5.4 tons | N/A | Air Source Split <5.4 tons | 10.5 | 14.3 | 7.5 | 10.5 | 14.3 | 7.5 |  |  | IECC 2021 or Federal Standard |  | Pumps | LargeOffice | 0.0001424 | 0.0001065
[13 empty] | Air Source | Packaged | <5.4 tons | N/A | Air Source Packaged <5.4 tons | 10.6 | 13.4 | 6.7 | 10.6 | 13.4 | 6.7 |  |  | IECC 2021 or Federal Standard |  | Pumps | MediumOffice | 0.0001365 | 0.0001109
| Water Source and Geothermal Heat Pumps - New Construction or Replacing Non-Functional Equipment | [11 empty] | Water Source | Water to Air | <17,000 Btu/h | N/A | Water Source Water to Air <17,000 Btu/h | 12.2 |  | 4.3 | 12.81 |  | 4.52 |  |  | IECC 2021 or Federal Standard |  | Pumps | Outpatient | 0.0001311 | 0.0001082
| Water Source and Geothermal Heat Pumps - Replacing functional equipment < 15 yrs old | [11 empty] | Water Source | Water to Air | ≥17,000 to <135,000 Btu/h | N/A | Water Source Water to Air ≥17,000 to <135,000 Btu/h | 13 |  | 4.3 | 13.65 |  | 4.52 |  |  | IECC 2021 or Federal Standard |  | Pumps | PrimarySchool | 0.0002209 | 0.0001292
| Ductless Mini-Split Heat Pump - Replace functional equipment < 15 yrs old | [11 empty] | Water Source | Water to Water | <135,000 Btu/h | N/A | Water Source Water to Water <135,000 Btu/h | 10.6 |  | 3.7 | 11.13 |  | 3.89 |  |  | IECC 2021 or Federal Standard |  | Pumps | QuickServiceRestaurant | 0.0001585 | 0.0001281
| Packaged Terminal Air Conditioner - New construction or replace non-functional | [11 empty] | Ground Source | Brine to Air | <135,000 Btu/h | Tier 1 | Ground Source Brine to Air <135,000 Btu/h | 14.1 |  | 3.2 | 14.81 |  | 3.36 | 15.51 | 3.52 | IECC 2021 or Federal Standard |  | Pumps | RetailStandalone | 0.0001189 | 0.0001334
| Packaged Terminal Air Conditioner - Replace functional equipment < 15 yrs old |  |  |  | Pump Motor HP | Motor Efficiency (%) | [6 empty] | Ground Source | Brine to Water | <135,000 Btu/h | Tier 1 | Ground Source Brine to Water <135,000 Btu/h | 12.1 |  | 2.5 | 12.71 |  | 2.63 | 13.31 | 2.75 | IECC 2021 or Federal Standard |  | Pumps | RetailStripmall | 0.0001385 | 0.00012
| Packaged Terminal Heat Pump - New construction or replace non-functional |  |  |  | 1 | 0.77 | [6 empty] | Groundwater Source | Water to Air | <135,000 Btu/h | Tier 1 | Groundwater Source Water to Air <135,000 Btu/h | 18 |  | 3.7 | 18.9 |  | 3.89 | 19.8 | 4.07 | IECC 2021 or Federal Standard |  | Pumps | SecondarySchool | 0.0001845 | 0.0001177
| Packaged Terminal Heat Pump - Replace functional equipment < 15 yrs old |  |  |  | 1.5 | 0.84 | [6 empty] | Groundwater Source | Water to Water | <135,000 Btu/h | Tier 1 | Groundwater Source Water to Water <135,000 Btu/h | 16.3 |  | 3.1 | 17.12 |  | 3.26 | 17.93 | 3.41 | IECC 2021 or Federal Standard |  | Pumps | SmallHotel | 0.0001016 | 0.000137
| Air-Cooled Chillers (Early Retirement) |  |  |  | 2 | 0.855 | [6 empty] | Mini-Split | Heat Pump | <5.4 tons | N/A | Mini-Split Heat Pump <5.4 tons | 10.5 | 14.3 | 7.5 | 11.2 | 15.2 | 7.8 |  |  | Federal Standard for Room AC & Gas Boilers |  | Pumps | SmallOffice | 0.000175 | 0.0001355
| Air-Cooled Chillers (Time of Sale) |  |  |  | 3 | 0.865 | [6 empty] | Cold Climate |  | <5.4 tons | N/A | Cold Climate <5.4 tons | 11.5 | 14.3 | 7.5 | 11.5 | 14.3 | 7.5 |  |  | IECC 2021 or Federal Standard |  | Pumps | Warehouse | 0.0001656 | 0.0001332
| Water-Cooled Chillers (Early Retirement) |  |  |  | 5 | 0.885 | [21 empty] | Pumps | Other | 0.000143 | 0.0001174
| Water-Cooled Chillers (Time of Sale) |  |  |  | 7.5 | 0.895 | [21 empty] | Refrigeration | FullServiceRestaurant | 0.0001421 | 0.0001082
| Variable Frequency Drives |  |  |  | 10 | 0.902 | [21 empty] | Refrigeration | Hospital | 0.0001533 | 0.0001163
| Dual Enthalpy Economizer Controls |  |  |  | 15 | 0.91 | [5 empty] | Equipment | Type | Compliance Path | Size Category | Options | Index Name | Full Load Base | IPLV Base | Qualifying Full Load | Qualifying IPLV | TRM/Source | [5 empty] | Refrigeration | LargeHotel | 0.0001374 | 0.0001115
| Smart Thermostat |  |  |  | 20 | 0.91 | [21 empty] | Refrigeration | PrimarySchool | 0.0001393 | 0.0001079
| Room Air Conditioner | [10 empty] | Chillers | Air Cooled | Path A | <150 tons | N/A | Air Cooled Path A <150 tons | 10.1 | 13.7 | 10.1 | 13.7 | IECC 2018 - Table C403.3.2(3) | [5 empty] | Refrigeration | QuickServiceRestaurant | 0.0001419 | 0.000107
[13 empty] | Air Cooled | Path A | ≥150 tons | N/A | Air Cooled Path A ≥150 tons | 10.1 | 14 | 10.1 | 14 | IECC 2018 - Table C403.3.2(3) | [5 empty] | Refrigeration | SecondarySchool | 0.000159 | 0.0001169
| Measure | Incentive |  |  | Water Source | Water to Air | [6 empty] | Air Cooled | Path B | <150 tons | N/A | Air Cooled Path B <150 tons | 9.7 | 15.8 | 9.7 | 15.8 | IECC 2018 - Table C403.3.2(3) | [5 empty] | Refrigeration | Other | 0.0001426 | 0.0001094
| Air Conditioners | 250 |  |  | Water Source | Water to Water | [6 empty] | Air Cooled | Path B | ≥150 tons | N/A | Air Cooled Path B ≥150 tons | 9.7 | 16.1 | 9.7 | 16.1 | IECC 2018 - Table C403.3.2(3) | [5 empty] | Ventilation | FullServiceRestaurant | 0.000157 | 0.0001388
| Air Source Heat Pumps | 250 |  |  | Water Source | Water to Water | [6 empty] | Water Cooled, Positive Displacement | Path A | <75 tons | N/A | Water Cooled, Positive Displacement Path A <75 tons | 0.75 | 0.6 | 0.75 | 0.6 | IECC 2018 - Table C403.3.2(3) | [5 empty] | Ventilation | Hospital | 0.0001181 | 0.0001114
| Water Source Heat Pumps | 250 |  |  | Ground Source | Brine to Air | [6 empty] | Water Cooled, Positive Displacement | Path A | ≥75 to <150 tons | N/A | Water Cooled, Positive Displacement Path A ≥75 to <150 tons | 0.72 | 0.56 | 0.72 | 0.56 | IECC 2018 - Table C403.3.2(3) | [5 empty] | Ventilation | LargeHotel | 0.0001254 | 0.0001455
| Ground Source Tier 1 | 300 |  |  | Ground Source | Brine to Water | [6 empty] | Water Cooled, Positive Displacement | Path A | ≥150 to <300 tons | N/A | Water Cooled, Positive Displacement Path A ≥150 to <300 tons | 0.66 | 0.54 | 0.66 | 0.54 | IECC 2018 - Table C403.3.2(3) | [5 empty] | Ventilation | LargeOffice | 0.0001379 | 0.0001377
| Ground Source Tier 2 | 350 |  |  | Groundwater Source | Water to Air | [6 empty] | Water Cooled, Positive Displacement | Path A | ≥300 to <600 tons | N/A | Water Cooled, Positive Displacement Path A ≥300 to <600 tons | 0.61 | 0.52 | 0.61 | 0.52 | IECC 2018 - Table C403.3.2(3) | [5 empty] | Ventilation | MediumOffice | 0.0001338 | 0.0001262
| Ductless Mini-Split Heat Pumps | 150 |  |  | Groundwater Source | Water to Water | [6 empty] | Water Cooled, Positive Displacement | Path A | ≥600 tons | N/A | Water Cooled, Positive Displacement Path A ≥600 tons | 0.56 | 0.5 | 0.56 | 0.5 | IECC 2018 - Table C403.3.2(3) | [5 empty] | Ventilation | Outpatient | 0.000147 | 0.000131
| PTAC/PTHP < 3/4 tons | 75 |  |  | Ground Source | Brine to Air | [6 empty] | Water Cooled, Positive Displacement | Path B | <75 tons | N/A | Water Cooled, Positive Displacement Path B <75 tons | 0.78 | 0.5 | 0.78 | 0.5 | IECC 2018 - Table C403.3.2(3) | [5 empty] | Ventilation | PrimarySchool | 0.0002077 | 0.0001931
| PTAC/PTHP > 3/4 tons & < 1 ton | 100 |  |  | Ground Source | Brine to Water | [6 empty] | Water Cooled, Positive Displacement | Path B | ≥75 to <150 tons | N/A | Water Cooled, Positive Displacement Path B ≥75 to <150 tons | 0.75 | 0.49 | 0.75 | 0.49 | IECC 2018 - Table C403.3.2(3) | [5 empty] | Ventilation | QuickServiceRestaurant | 0.0001474 | 0.0001358
| PTAC/PTHP > 1 ton | 125 |  |  | Groundwater Source | Water to Air | [6 empty] | Water Cooled, Positive Displacement | Path B | ≥150 to <300 tons | N/A | Water Cooled, Positive Displacement Path B ≥150 to <300 tons | 0.68 | 0.44 | 0.68 | 0.44 | IECC 2018 - Table C403.3.2(3) | [5 empty] | Ventilation | RetailStandalone | 0.0001483 | 0.0001323
| Chillers | 30 | $30/ton + additional $10 for each 0.1 EER above or 0.01 kW below minimum efficiency |  | Groundwater Source | Water to Water | [6 empty] | Water Cooled, Positive Displacement | Path B | ≥300 to <600 tons | N/A | Water Cooled, Positive Displacement Path B ≥300 to <600 tons | 0.625 | 0.41 | 0.625 | 0.41 | IECC 2018 - Table C403.3.2(3) | [5 empty] | Ventilation | RetailStripmall | 0.0001606 | 0.0001246
| Smart Thermostat | 100 | [10 empty] | Water Cooled, Positive Displacement | Path B | ≥600 tons | N/A | Water Cooled, Positive Displacement Path B ≥600 tons | 0.585 | 0.38 | 0.585 | 0.38 | IECC 2018 - Table C403.3.2(3) | [5 empty] | Ventilation | SecondarySchool | 0.0001513 | 0.0001569
| Dual Enthalpy Economizers | 250 | [10 empty] | Water Cooled, Centrifugal | Path A | <150 tons | N/A | Water Cooled, Centrifugal Path A <150 tons | 0.61 | 0.55 | 0.61 | 0.55 | IECC 2018 - Table C403.3.2(3) | [5 empty] | Ventilation | SmallHotel | 0.0001273 | 0.00012
| Room AC | 25 | [10 empty] | Water Cooled, Centrifugal | Path A | ≥150 to <300 tons | N/A | Water Cooled, Centrifugal Path A ≥150 to <300 tons | 0.61 | 0.55 | 0.61 | 0.55 | IECC 2018 - Table C403.3.2(3) | [5 empty] | Ventilation | SmallOffice | 0.0001377 | 0.0001338
| VFDs | See "VFD Lookup" Tab | [10 empty] | Water Cooled, Centrifugal | Path A | ≥300 to <400 tons | N/A | Water Cooled, Centrifugal Path A ≥300 to <400 tons | 0.56 | 0.52 | 0.56 | 0.52 | IECC 2018 - Table C403.3.2(3) | [5 empty] | Ventilation | Warehouse | 0.000131 | 0.0001541
| ECM Circulating Fan | 0 | [10 empty] | Water Cooled, Centrifugal | Path A | ≥400 to <600 tons | N/A | Water Cooled, Centrifugal Path A ≥400 to <600 tons | 0.56 | 0.5 | 0.56 | 0.5 | IECC 2018 - Table C403.3.2(3) | [5 empty] | Ventilation | Other | 0.0001453 | 0.0001347
| ECM Circulator Pump | 0 | [10 empty] | Water Cooled, Centrifugal | Path A | ≥600 tons | N/A | Water Cooled, Centrifugal Path A ≥600 tons | 0.56 | 0.5 | 0.56 | 0.5 | IECC 2018 - Table C403.3.2(3) | [5 empty] | Water Heating | FullServiceRestaurant | 0.0001607 | 0.0001575
| Chiller Tune Up | 0 | [10 empty] | Water Cooled, Centrifugal | Path B | <150 tons | N/A | Water Cooled, Centrifugal Path B <150 tons | 0.695 | 0.44 | 0.695 | 0.44 | IECC 2018 - Table C403.3.2(3) | [5 empty] | Water Heating | Hospital | 0.0001025 | 0.0001327
| Switch Reluctance Motor | 0 | [10 empty] | Water Cooled, Centrifugal | Path B | ≥150 to <300 tons | N/A | Water Cooled, Centrifugal Path B ≥150 to <300 tons | 0.635 | 0.4 | 0.635 | 0.4 | IECC 2018 - Table C403.3.2(3) | [5 empty] | Water Heating | LargeHotel | 8.66e-05 | 0.0001224
| Hotel Room Occ Sensor | 0 | [10 empty] | Water Cooled, Centrifugal | Path B | ≥300 to <400 tons | N/A | Water Cooled, Centrifugal Path B ≥300 to <400 tons | 0.595 | 0.39 | 0.595 | 0.39 | IECC 2018 - Table C403.3.2(3) | [5 empty] | Water Heating | LargeOffice | 0.0001298 | 0.0001573
| Low-e Film | 0 | [10 empty] | Water Cooled, Centrifugal | Path B | ≥400 to <600 tons | N/A | Water Cooled, Centrifugal Path B ≥400 to <600 tons | 0.585 | 0.38 | 0.585 | 0.38 | IECC 2018 - Table C403.3.2(3) | [5 empty] | Water Heating | MediumOffice | 0.0001319 | 0.0001592
| VRF Heat Pump | 0 | [10 empty] | Water Cooled, Centrifugal | Path B | ≥600 tons | N/A | Water Cooled, Centrifugal Path B ≥600 tons | 0.585 | 0.38 | 0.585 | 0.38 | IECC 2018 - Table C403.3.2(3) | [5 empty] | Water Heating | Outpatient | 0.00013 | 0.0001197
[28 empty] | Water Heating | PrimarySchool | 0.0001762 | 0.0002184
| Units | [10 empty] | Equipment | Type | Subcategory | Size Category | Options | Index Name | Baseline_COP__c | Factor_2__c | Not used | [7 empty] | Water Heating | QuickServiceRestaurant | 0.0001632 | 0.0001754
| SEER | SEER/HSPF | EER/SEER/HSPF | [24 empty] | Water Heating | RetailStripmall | 0.000163 | 0.0001525
| SEER2 | SEER2/HSPF2 | EER2/SEER2/HSPF2 | [8 empty] | Smart Thermostat - Heating | Air Source Heat Pump | N/A | <65,000 Btu/h | N/A | Air Source Heat Pump <65,000 Btu/h | 2.4033 | 1 | [8 empty] | Water Heating | SecondarySchool | 7.66e-05 | 0.0002029
[13 empty] | Air Source Heat Pump | N/A | ≥65,000 to <135,000 Btu/h | N/A | Air Source Heat Pump ≥65,000 to <135,000 Btu/h | 3.3 | 1 | [8 empty] | Water Heating | SmallHotel | 7.5e-05 | 0.0001386
| Phase | [11 empty] | Air Source Heat Pump | N/A | ≥135,000 to <240,000 Btu/h | N/A | Air Source Heat Pump ≥135,000 to <240,000 Btu/h | 3.2 | 1 | [8 empty] | Water Heating | SmallOffice | 0.0001971 | 0.0001986
| Single Phase | [11 empty] | Air Source Heat Pump | N/A | ≥240,000 to ≤300,000 Btu/h | N/A | Air Source Heat Pump ≥240,000 to ≤300,000 Btu/h | 3.2 | 1 | [8 empty] | Water Heating | Other | 0.00014 | 0.0001563
| Three Phase | [11 empty] | Electric Resistance | N/A | <65,000 Btu/h | N/A | Electric Resistance <65,000 Btu/h | 1 | 1 | [8 empty] | Whole Building Electric | FullServiceRestaurant | 0.0002208 | 0.0002208
[13 empty] | Electric Resistance | N/A | ≥65,000 to <135,000 Btu/h | N/A | Electric Resistance ≥65,000 to <135,000 Btu/h | 1 | 1 | [8 empty] | Whole Building Electric | Hospital | 0.0001486 | 0.0001501
| Product Type | Subcategory | FLH cool | FLH heat | Desuperheater? | %DHWDisplaced | Electric water heater size | [5 empty] | Electric Resistance | N/A | ≥135,000 to <240,000 Btu/h | N/A | Electric Resistance ≥135,000 to <240,000 Btu/h | 1 | 1 | [8 empty] | Whole Building Electric | LargeHotel | 0.0001601 | 0.0001601
| Water-to-air | Closed Loop | 712 | 885 | Yes | 0.44 | <= 55 gallon | [5 empty] | Electric Resistance | N/A | ≥240,000 to ≤300,000 Btu/h | N/A | Electric Resistance ≥240,000 to ≤300,000 Btu/h | 1 | 1 | [8 empty] | Whole Building Electric | LargeOffice | 0.0001822 | 0.0001822
| Water-to-water | Open Loop |  |  | No | 0 | > 55 gallon | [5 empty] | None | N/A | <65,000 Btu/h | N/A | None <65,000 Btu/h | 3.3 | 0 | [8 empty] | Whole Building Electric | MediumOffice | 0.0002088 | 0.0002088
|  | Direct Geoexchange-to-air | [10 empty] | None | N/A | ≥65,000 to <135,000 Btu/h | N/A | None ≥65,000 to <135,000 Btu/h | 3.3 | 0 | [8 empty] | Whole Building Electric | Outpatient | 0.000216 | 0.000216
[13 empty] | None | N/A | ≥135,000 to <240,000 Btu/h | N/A | None ≥135,000 to <240,000 Btu/h | 3.3 | 0 | [8 empty] | Whole Building Electric | PrimarySchool | 0.0002835 | 0.0002862
| Product Type | Subcategory | [10 empty] | None | N/A | ≥240,000 to ≤300,000 Btu/h | N/A | None ≥240,000 to ≤300,000 Btu/h | 3.3 | 0 | [8 empty] | Whole Building Electric | QuickServiceRestaurant | 0.0002018 | 0.0002018
| Water-to-air | Closed Loop | [10 empty] | Non-Electric | N/A | <65,000 Btu/h | N/A | Non-Electric <65,000 Btu/h | 3.3 | 0 | [8 empty] | Whole Building Electric | RetailStandalone | 0.0002438 | 0.0002438
| Water-to-air | Open Loop | [10 empty] | Non-Electric | N/A | ≥65,000 to <135,000 Btu/h | N/A | Non-Electric ≥65,000 to <135,000 Btu/h | 3.3 | 0 | [8 empty] | Whole Building Electric | RetailStripmall | 0.0002407 | 0.0002407
| Water-to-air | Direct Geoexchange-to-air | [10 empty] | Non-Electric | N/A | ≥135,000 to <240,000 Btu/h | N/A | Non-Electric ≥135,000 to <240,000 Btu/h | 3.3 | 0 | [8 empty] | Whole Building Electric | SecondarySchool | 0.0002423 | 0.0002423
| Water-to-water | Closed Loop | [10 empty] | Non-Electric | N/A | ≥240,000 to ≤300,000 Btu/h | N/A | Non-Electric ≥240,000 to ≤300,000 Btu/h | 3.3 | 0 | [8 empty] | Whole Building Electric | SmallHotel | 0.0001685 | 0.0001685
| Water-to-water | Open Loop | [9 empty] | Equipment | Type | Subcategory | Size Category | Options | Index Name | Baseline_SEER__c | Factor_1__c | [8 empty] | Whole Building Electric | SmallOffice | 0.0002369 | 0.0002369
| Water-to-water | Direct Geoexchange-to-air | [25 empty] | Whole Building Electric | Warehouse | 0.000168 | 0.0002018
[12 empty] | Smart Thermostat - Cooling | Air Source Air Conditioner | N/A | <65,000 Btu/h | N/A | Air Source Air Conditioner <65,000 Btu/h | 14 | 1 | [8 empty] | Whole Building Electric | Other | 0.0002077 | 0.000209
| GSHP Baseline | [11 empty] | Air Source Air Conditioner | N/A | ≥65,000 to <135,000 Btu/h | N/A | Air Source Air Conditioner ≥65,000 to <135,000 Btu/h | 12.9 | 1 | [8 empty] | https://docs.google.com/spreadsheets/d/1FgV3jdR4Miewktd9anaxV-Z49ahTZl9a/edit#gid=1808156398
EER | SEER | EER | HSPF | COP | [8 empty] | Air Source Air Conditioner | N/A | ≥135,000 to <240,000 Btu/h | N/A | Air Source Air Conditioner ≥135,000 to <240,000 Btu/h | 12.4 | 1
| 14 | 11.8 | 8.2 | 2.4 | [8 empty] | Air Source Air Conditioner | N/A | ≥240,000 to ≤300,000 Btu/h | N/A | Air Source Air Conditioner ≥240,000 to ≤300,000 Btu/h | 11.6 | 1
[13 empty] | Water Cooled Air Conditioner | N/A | <65,000 Btu/h | N/A | Water Cooled Air Conditioner <65,000 Btu/h | 12.3 | 1
| Product Type | Closed Loop | Open Loop | Direct Geoexchange-to-air | [8 empty] | Water Cooled Air Conditioner | N/A | ≥65,000 to <135,000 Btu/h | N/A | Water Cooled Air Conditioner ≥65,000 to <135,000 Btu/h | 13.9 | 1
COP | Water-to-air | 17.1 | 21.1 | 16 | [8 empty] | Water Cooled Air Conditioner | N/A | ≥135,000 to <240,000 Btu/h | N/A | Water Cooled Air Conditioner ≥135,000 to <240,000 Btu/h | 13.9 | 1
| Water-to-water | 16.1 | 20.1 | 15 | [8 empty] | Water Cooled Air Conditioner | N/A | ≥240,000 to ≤300,000 Btu/h | N/A | Water Cooled Air Conditioner ≥240,000 to ≤300,000 Btu/h | 13.6 | 1
[13 empty] | Air Source Heat Pump | N/A | <65,000 Btu/h | N/A | Air Source Heat Pump <65,000 Btu/h | 14 | 1
| Product Type | Closed Loop | Open Loop | Direct Geoexchange-to-air | [8 empty] | Air Source Heat Pump | N/A | ≥65,000 to <135,000 Btu/h | N/A | Air Source Heat Pump ≥65,000 to <135,000 Btu/h | 12.2 | 1
| Water-to-air | 3.6 | 4.1 | 3.6 | [8 empty] | Air Source Heat Pump | N/A | ≥135,000 to <240,000 Btu/h | N/A | Air Source Heat Pump ≥135,000 to <240,000 Btu/h | 11.6 | 1
| Water-to-water | 3.1 | 3.5 | 3.1 | [8 empty] | Air Source Heat Pump | N/A | ≥240,000 to ≤300,000 Btu/h | N/A | Air Source Heat Pump ≥240,000 to ≤300,000 Btu/h | 10.6 | 1
[13 empty] | None | N/A | <65,000 Btu/h | N/A | None <65,000 Btu/h | 14 | 0
| Baseline Condition | [11 empty] | None | N/A | ≥65,000 to <135,000 Btu/h | N/A | None ≥65,000 to <135,000 Btu/h | 14 | 0
| Time of Sale | [11 empty] | None | N/A | ≥135,000 to <240,000 Btu/h | N/A | None ≥135,000 to <240,000 Btu/h | 14 | 0
| Early Replacement | [11 empty] | None | N/A | ≥240,000 to ≤300,000 Btu/h | N/A | None ≥240,000 to ≤300,000 Btu/h | 14 | 0 | [7 empty] | Qualifying HSPF2 | Qualifying COP
| GSHP & WSHP | [10 empty] | Equipment | Type | Subcategory | Size Category | Index Name | SEER | SEER2 as of 1/1/25 | IEER | HSPF | HSPF2 starting 1/1/25 | COP | Qualifying SEER | Qualifying SEER2 | Qualifying IEER | Qualifying HSPF | 7.875
| Replace on Burnout | [26 empty] | 3.465
| New Construction | [10 empty] | VRF | Air Cooled | With Heat Recovery | <65000 Btu/h | Air CooledWith Heat Recovery<65000 Btu/h | 13 | 13.4 |  | 7.7 | 7.5 |  | 13.65 | 14.07 |  | 8.085 |  | 3.36
| Early Replacement | [11 empty] | Air Cooled | With Heat Recovery | ≥65000 to <135000 Btu/h | Air CooledWith Heat Recovery≥65000 to <135000 Btu/h |  |  | 14.4 |  |  | 3.3 |  |  | 15.12 |  |  | 3.36
[13 empty] | Air Cooled | With Heat Recovery | ≥130000 to <240000 Btu/h | Air CooledWith Heat Recovery≥130000 to <240000 Btu/h |  |  | 13.7 |  |  | 3.2 |  |  | 14.385 |  | 7.875
| Smart Thermostat | [11 empty] | Air Cooled | With Heat Recovery | ≥240000 | Air CooledWith Heat Recovery≥240000 |  |  | 12.5 |  |  | 3.2 |  |  | 13.125 |  |  | 3.465
| Time of Sale | [11 empty] | Air Cooled | Without Heat Recovery | <65000 Btu/h | Air CooledWithout Heat Recovery<65000 Btu/h | 13 | 13.4 |  | 7.7 | 7.5 |  | 13.65 | 14.07 |  | 8.085 |  | 3.36
| Retrofit | [11 empty] | Air Cooled | Without Heat Recovery | ≥65000 to <135000 Btu/h | Air CooledWithout Heat Recovery≥65000 to <135000 Btu/h |  |  | 14.6 |  |  | 3.3 |  |  | 15.33 |  |  | 3.36
| New Construction | [11 empty] | Air Cooled | Without Heat Recovery | ≥130000 to <240000 Btu/h | Air CooledWithout Heat Recovery≥130000 to <240000 Btu/h |  |  | 13.9 |  |  | 3.2 |  |  | 14.595 |  |  | 4.515
[13 empty] | Air Cooled | Without Heat Recovery | ≥240000 | Air CooledWithout Heat Recovery≥240000 |  |  | 12.7 |  |  | 3.2 |  |  | 13.335 |  |  | 4.515
| ECM Circulator Pump | [11 empty] | Water Cooled | With Heat Recovery | <65000 Btu/h | Water CooledWith Heat Recovery<65000 Btu/h |  |  | 15.8 |  |  | 4.3 |  |  | 16.59 |  |  | 4.2
| Time of Sale | [11 empty] | Water Cooled | With Heat Recovery | ≥65000 to <135000 Btu/h | Water CooledWith Heat Recovery≥65000 to <135000 Btu/h |  |  | 15.8 |  |  | 4.3 |  |  | 16.59 |  |  | 4.095
| Early Replacement | [11 empty] | Water Cooled | With Heat Recovery | ≥130000 to <240000 Btu/h | Water CooledWith Heat Recovery≥130000 to <240000 Btu/h |  |  | 13.8 |  |  | 4 |  |  | 14.49 |  |  | 4.515
| New Construction | [11 empty] | Water Cooled | With Heat Recovery | ≥240000 | Water CooledWith Heat Recovery≥240000 |  |  | 11.8 |  |  | 3.9 |  |  | 12.39 |  |  | 4.515
[13 empty] | Water Cooled | Without Heat Recovery | <65000 Btu/h | Water CooledWithout Heat Recovery<65000 Btu/h |  |  | 16 |  |  | 4.3 |  |  | 16.8 |  |  | 4.2
[13 empty] | Water Cooled | Without Heat Recovery | ≥65000 to <135000 Btu/h | Water CooledWithout Heat Recovery≥65000 to <135000 Btu/h |  |  | 16 |  |  | 4.3 |  |  | 16.8 |  |  | 4.095
[13 empty] | Water Cooled | Without Heat Recovery | ≥130000 to <240000 Btu/h | Water CooledWithout Heat Recovery≥130000 to <240000 Btu/h |  |  | 14 |  |  | 4 |  |  | 14.7
[13 empty] | Water Cooled | Without Heat Recovery | ≥240000 | Water CooledWithout Heat Recovery≥240000 |  |  | 12 |  |  | 3.9 |  |  | 12.6
Note on U89: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: EER2 based on Federal Standards, from MD Res TRM
Note on T98: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: These efficiency ratings are in EER2, SEER2, and HSPF2
Note on W103: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: From filing: "Meets or exceeds the requirements presented in the applicable International Energy Conservation Code or MD TRM"

## Misc Lookups (hidden)
Low-e Film
Window Film Deemed Savings
Building Type | Hagerstown (kWh/100 SF) | Hagerstown (Therms/100 SF) | Mapped ETDF Bldg Type
Assembly | 547 | -64.5 | Other
Auto Repair | 251 | -85.4 | SmallOffice
Big Box Retail | 497 | -42.7 | RetailStandalone
Fast Food Restaurant | 363 | -80 | QuickServiceRestaurant
Full-Service Restaurant | 373 | -104.9 | FullServiceRestaurant
Grocery | 497 | -42.7 | RetailStandalone
Light Industrial | 232 | -75.7 | Warehouse
Motel | 484 | -21.9 | SmallHotel
Primary School | 513 | -108.4 | PrimarySchool
Small Office | 547 | -64.5 | SmallOffice
Small Retail | 414 | -69.1 | RetailStripmall
Warehouse | 567 | -92.7 | Warehouse
Other | 440 | -71 | Other
Building Type | Installed Area of Film (ft2) | kWh/100 SF savings | Therms/100 SF savings | kWh/yr savings | Therms/yr savings | MMBtu/yr savings | ETDF Bldg Type | ETDF Summer Peak | ETDF Winter Peak | Summer Peak kW savings | Winter Peak kW savings | Incentive
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF! |  |  |  | 0
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF! |  |  |  | 0
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF! |  |  |  | 0
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF! |  |  |  | 0
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF! |  |  |  | 0
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF! |  |  |  | 0
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF! |  |  |  | 0
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF! |  |  |  | 0
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF! |  |  |  | 0
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF! |  |  |  | 0
Switch Reluctance Motor
RTU Compressor Type | ESF fan
Single Stage | 58.5%
Single Two Stage | 76.6%
Variable Speed Compressor | 81.3%
Building Type | Total Fan Run Hours | Mapped ETDF Bldg Type
Assembly | 7176 | Other
Assisted Living | 8760 | Hospital
Auto Dealership | 7391 | RetailStripmall
College | 4797 | SecondarySchool
Convenience Store | 6947 | RetailStandalone
Drug Store | 7098 | RetailStandalone
Elementary School | 3734 | PrimarySchool
Emergency Services | 8760 | Other
Garage | 7297 | RetailStandalone
Grocery | 8474 | RetailStandalone
Healthcare Clinic | 4279 | Outpatient
High School | 3432 | SecondarySchool
Manufacturing Facility | 8760 | Warehouse
Multi Family - High Rise | 8760 | LargeHotel
Multi Family - Mid Rise | 8760 | LargeHotel
Hotel/Motel - Guest | 2389 | LargeHotel
Hotel/Motel - Common | 8612 | LargeHotel
Movie Theater | 7444 | Other
Office - Low Rise | 6293 | SmallOffice
Office - Mid Rise | 3412 | LargeOffice
Religious Building | 7320 | SmallOffice
Restaurant | 7243 | FullServiceRestaurant
Retail - Department Store | 7097 | RetailStandalone
Retail - Strip Mall | 6865 | RetailStripmall
Warehouse | 6777 | Warehouse
Unknown | 6190 | Other
Fan Quantity | RTU Fan hp | RTU Compressor Type | Total Fan Run Hours | ESF Fan | kWh/yr savings | ETDF Bldg Type | ETDF Summer | ETDF winter | Peak kW savings summer | Peak kW savings winter | Incentive
#REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! |  | #REF! | #REF!
ECM Circulation Fan
Motor Type | Assumed Efficiency |  | LF | 0.9
SP | 0.4 |  | Default ventilation hours, hrs/yr | 0
PSC | 0.5 |  | IF kWh | 26.2%
ECM | 0.85
Building Type | Fan Quantity | Baseline Fan horsepower (hp) | Baseline Fan Motor Type | ECM Fan horsepower (hp) | Baseline motor efficiency | ECM Motor efficiency | Baseline Fan wattage (W) | ECM Fan wattage (W) | EFLH heat | EFLH cool | kWh heat savings | kWh cool savings | kWh vent savings | Total kWh/yr savings | ETDF Bldg Type | ETDF summer | ETDF winter | Summer Peak kW savings | Winter Peak kW savings | Incentive
|  |  | 0 |  |  | 0.85 | [8 empty] | #N/A
|  |  | 0 |  |  | 0.85 | [8 empty] | #N/A
|  |  | 0 |  |  | 0.85 | [8 empty] | #N/A
|  |  | 0 |  |  | 0.85 | [8 empty] | #N/A
|  |  | 0 |  |  | 0.85 | [8 empty] | #N/A
|  |  | 0 |  |  | 0.85 | [8 empty] | #N/A
|  |  | 0 |  |  | 0.85 | [8 empty] | #N/A
|  |  | 0 |  |  | 0.85 | [8 empty] | #N/A
|  |  | 0 |  |  | 0.85 | [8 empty] | #N/A
|  |  | 0 |  |  | 0.85 | [8 empty] | #N/A
ECM Circulator Pumps
Pump Application | Pump Control | Motor Efficiency | 85% |  | Control Type | HOU DHW
Heating Circulation | Continuously Running | ECM to baseline watts | 18% |  | Continuously Running | 8760
DHW Recirculation | Aquastat-Controlled | LF | 0.9 |  | Aquastat-Controlled | 2190
Building Type | Project Type | Pump Application | Pump Quantity | Baseline Pump Motor Horsepower (hp) | Baseline Pump Control | ECM Horsepower (hp) | ECM Pump Control | Baseline Pump Motor Wattage (W) | ECM Wattage (W) | EFLH heat | HOU DHW base | HOU DHW EE | ETDF Bldg Type | ETDF Summer | ETDF Winter | DHW savings kWh/yr | Heating Circulation kWh/yr savings | kWh/yr savings | Summer Peak kW savings | Winter Peak kW savings | Incentive
|  | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  |  | #N/A |  |  |  |  | 0 | #VALUE! | #VALUE! | 0
|  | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  |  | #N/A |  |  |  |  | 0 | #VALUE! | #VALUE! | 0
|  | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  |  | #N/A |  |  |  |  | 0 | #VALUE! | #VALUE! | 0
|  | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  |  | #N/A |  |  |  |  | 0 | #VALUE! | #VALUE! | 0
|  | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  |  | #N/A |  |  |  |  | 0 | #VALUE! | #VALUE! | 0
|  | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  |  | #N/A |  |  |  |  | 0 | #VALUE! | #VALUE! | 0
|  | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  |  | #N/A |  |  |  |  | 0 | #VALUE! | #VALUE! | 0
|  | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  |  | #N/A |  |  |  |  | 0 | #VALUE! | #VALUE! | 0
|  | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  |  | #N/A |  |  |  |  | 0 | #VALUE! | #VALUE! | 0
|  | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  |  | #N/A |  |  |  |  | 0 | #VALUE! | #VALUE! | 0
Chiller Tune Up
ESF | 0.045
Building Type | Chiller Quantity | Rated Tons | IPLV | EFLH cool | ETDF Bldg Type | ETDF summer | ETDF winter | kWh savings | kW summer peak savings | kW winter peak savings | Incentive
#REF! | #REF! | #REF! | #REF! |  | #REF! |  | 0
#REF! | #REF! | #REF! | #REF! |  | #REF! |  | 0
#REF! | #REF! | #REF! | #REF! |  | #REF! |  | 0
#REF! | #REF! | #REF! | #REF! |  | #REF! |  | 0
#REF! | #REF! | #REF! | #REF! |  | #REF! |  | 0
#REF! | #REF! | #REF! | #REF! |  | #REF! |  | 0
#REF! | #REF! | #REF! | #REF! |  | #REF! |  | 0
#REF! | #REF! | #REF! | #REF! |  | #REF! |  | 0
#REF! | #REF! | #REF! | #REF! |  | #REF! |  | 0
#REF! | #REF! | #REF! | #REF! |  | #REF! |  | 0
Hotel Room Occ Sensors
Hotel | Motel |  | Existing Setback Type
PTAC with Electric Resistance Heating | PTAC with Electric Resistance Heating |  | Housekeeping Setback
PTAC with Gas Heating | PTAC with Gas Heating |  | No Housekeeping Setback
PTHP | PTHP
Central Hot Water Fan Coil with Electric Resistance Heating
Central Hot Water Fan Coil with Gas Heating
Motel
| ESF (kWh/Ton) |  | GSF (Therms/Ton) |  |  | ETDF Summer | 0.000692
HVAC Type | Housekeeping Setback | No Housekeeping Setback | Housekeeping Setback | No Housekeeping Setback |  | ETDF winter | 0
PTAC with Electric Resistance Heating | 635 | 1986 | 0 | 0
PTAC with Gas Heating | 64 | 205 | 25 | 78
PTHP | 265 | 1002 | 0 | 0
Hotel
| ESF (kWh/Ton) |  | GSF (Therms/Ton) |  |  | ETDF Summer | 0.0004755
HVAC Type | Housekeeping Setback | No Housekeeping Setback | Housekeeping Setback | No Housekeeping Setback |  | ETDF winter | 0
PTAC with Electric Resistance Heating | 236 | 429 | 0 | 0
PTAC with Gas Heating | 149 | 245 | 3.8 | 8.2
PTHP | 182 | 314 | 0 | 0
Central Hot Water Fan Coil with Electric Resistance Heating | 202 | 369 | 0 | 0
Central Hot Water Fan Coil with Gas Heating | 115 | 184 | 3.8 | 8.2
Building Type | Guest Room Quantity | Baseline Setback Type | HVAC Type | HVAC Unit Cooling Capacity (Tons) | ESF | GSF | kWh/yr savings | ETDF Summer | ETDF Winter | Summer Peak kW savings | Winter Peak kW savings | Therms/yr savings | MMBtu/yr savings | Incentive
#REF! | #REF! | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF!
VRF Heat Pumps
Equipment Type | Heat Recovery?
VRF - Air Cooled | Yes
VRF - Water Cooled | No

## VFD Lookup (hidden)
Default Fan Duty Cycle |  |  |  |  | Motor HP | Incentive | Units | HVAC Pump VFD Savings Factors |  | Part Load Ratios by Control and Fan Type and Flow Fractions (PLR)
Flow Fraction (% of Design CFM) |  | % of Time at Flow Fraction (%FF) |  |  | 2 | 500 | Per unit | System | ESF | Control Type | Flow Fraction | [9 empty] | Σ(%FF * PLR)
Min | Max |  |  |  | 3 | 600 | Per unit | Chilled Water Pump | 0.633 |  | 10% | 20% | 30% | 40% | 50% | 60% | 70% | 80% | 90% | 100%
0 | 10 | 0% |  |  | 4 | 700 | Per unit | Hot Water Pump | 0.652 | % of Time at Flow Fraction (%FF) | 0% | 1% | 5.5% | 15.5% | 22% | 25% | 19% | 8.5% | 3% | 0.5%
10 | 20 | 1% |  |  | 5 | 800 | Per unit | Source: Maryland TRM V10, pg. 301 |  | No Control or Bypass Damper | [10 empty] | 1 | bar: Flow Fraction 10% to Flow Fraction 100%
20 | 30 | 5.5% |  |  | 7.5 | 900 | Per unit |  |  | Discharge Dampers | 0.46 | 0.55 | 0.63 | 0.7 | 0.77 | 0.83 | 0.88 | 0.93 | 0.97 | 1 | 0.8059
30 | 40 | 15.5% |  |  | 10 | 1100 | Per unit |  |  | Outlet Damper, BI & Airfoil Fans | 0.53 | 0.53 | 0.57 | 0.64 | 0.72 | 0.8 | 0.89 | 0.96 | 1.02 | 1.05 | 0.7808
40 | 50 | 22% |  |  | 15 | 1350 | Per unit | VFD Application |  | Inlet Damper Box | 0.56 | 0.6 | 0.62 | 0.64 | 0.66 | 0.69 | 0.74 | 0.81 | 0.92 | 1.07 | 0.6994
50 | 60 | 25% |  |  | 20 | 1500 | Per unit | Fan |  | Inlet Guide Vane, BI & Airfoil Fans | 0.53 | 0.56 | 0.57 | 0.59 | 0.6 | 0.62 | 0.67 | 0.74 | 0.85 | 1 | 0.6361
60 | 70 | 19% |  |  | 25 | 1600 | Per unit | Chilled Water Pump |  | Inlet Vane Dampers | 0.38 | 0.4 | 0.42 | 0.44 | 0.48 | 0.53 | 0.6 | 0.7 | 0.83 | 0.99 | 0.53675
70 | 80 | 8.5% |  |  | 30 | 1800 | Per unit | Heating Hot Water Pump |  | Outlet Damper, FC Fans | 0.22 | 0.26 | 0.3 | 0.37 | 0.45 | 0.54 | 0.65 | 0.77 | 0.91 | 1.06 | 0.532
80 | 90 | 3% |  |  | 40 | 2000 | Per unit |  |  | Eddy Current Drives | 0.17 | 0.2 | 0.25 | 0.32 | 0.41 | 0.51 | 0.63 | 0.76 | 0.9 | 1.04 | 0.49955
90 | 100 | 0.5% |  |  | 50 | 2500 | Per unit |  |  | Inlet Guide Vane, FC Fans | 0.21 | 0.22 | 0.23 | 0.26 | 0.31 | 0.39 | 0.49 | 0.63 | 0.81 | 1.04 | 0.397
Source: Maryland TRM V11, pg. 133 |  |  |  |  | 60 | 3000 | Per unit |  |  | VFD with duct static pressure controls | 0.09 | 0.1 | 0.11 | 0.15 | 0.2 | 0.29 | 0.41 | 0.57 | 0.76 | 1.01 | 0.301
[5 empty] | 75 | 3750 | Per unit |  |  | VFD with Low/No Duct Static Pressure (<1" w.g.) | 0.05 | 0.06 | 0.09 | 0.12 | 0.18 | 0.27 | 0.39 | 0.55 | 0.75 | 1 | 0.2796
[5 empty] | 100 | 5000 | Per unit |  |  | Source: Maryland TRM V11, pg. 133-134
VFD Operating Hours by Application and Building Type (RHRSbase) |  |  |  |  | >100 to <200 | 50 | Per HP
Facility Type | Fan Motor Hours | Chilled Water Pumps | Heating Pumps | Mapped ETDF Bldg Type | [5 empty] | Calc Name | Flow Fraction 10%: Data Export Name
Auto Related | 6421 | 1442 | 2484 | SmallOffice | [5 empty] | Fan | Flow Fraction 10%: Fan
Bakery | 4618 | 1037 | 1787 | Other | [5 empty] | Chilled Water Pump | Flow Fraction 10%: Chilled Water Pump
Banks, Financial Centers | 5519 | 2732 | 5629 | SmallOffice | [5 empty] | Heating Hot Water Pump | Flow Fraction 10%: Hot Water Pump
Church | 3493 | 785 | 1351 | SmallOffice | [5 empty] | No Control or Bypass Damper | Flow Fraction 10%: No Control
College - Cafeteria | 5835 | 1311 | 2258 | QuickServiceRestaurant | [5 empty] | Discharge Dampers | Flow Fraction 10%: Discharge Damper
College - Classes/Administrative | 5995 | 2357 | 6471 | SecondarySchool | [5 empty] | Outlet Damper, BI & Airfoil Fans | Flow Fraction 10%: Outlet Damper or Airfoil Fans
College - Dormitory | 3833 | 3833 | 3833 | LargeHotel | [5 empty] | Inlet Damper Box | Flow Fraction 10%: Inlet Damper Box
Commercial Condos | 8760 | 4470 | 8760 | LargeHotel | [5 empty] | Inlet Guide Vane, BI & Airfoil Fans | Flow Fraction 10%: Inlet Guide Vane
Convenience Stores | 5207 | 1170 | 2015 | RetailStandalone | [5 empty] | Inlet Vane Dampers | Flow Fraction 10%: Inlet Vane Dampers
Convention Center | 8760 | 4470 | 8760 | Other | [5 empty] | Outlet Damper, FC Fans | Flow Fraction 10%: Outlet Damper or FC Fans
Court House | 5519 | 2732 | 5629 | SmallOffice | [5 empty] | Eddy Current Drives | Flow Fraction 10%: Eddy Current Drives
Dining: Bar Lounge/Leisure | 5264 | 1183 | 2037 | FullServiceRestaurant | [5 empty] | Inlet Guide Vane, FC Fans | Flow Fraction 10%: Inlet Guide Vane or FC Fans
Dining: Cafeteria/Fast Food | 5835 | 1311 | 2258 | QuickServiceRestaurant | [5 empty] | VFD with duct static pressure controls | Flow Fraction 10%: VFD with duct static pressure controls
Dining: Family | 5264 | 1183 | 2037 | FullServiceRestaurant | [5 empty] | VFD with Low/No Duct Static Pressure (<1" w.g.) | Flow Fraction 10%: VFD with Low/No Duct Static Pressure (<1" w.g.)
Entertainment | 5737 | 1289 | 2220 | Other
Exercise Center | 5737 | 1289 | 2220 | Other
Fast Food Restaurants | 5835 | 1311 | 2258 | QuickServiceRestaurant
Fire Station (Unmanned) | 3833 | 3833 | 3833 | Other
Food Stores | 4545 | 1021 | 1758 | RetailStripmall
Gymnasium | 5737 | 1289 | 2220 | Other
Hospitals | 8683 | 7682 | 8760 | Hospital
Hospitals/Health Care | 8683 | 7682 | 8760 | Hospital
Industrial - 1 Shift | 4618 | 1037 | 1787 | Warehouse
Industrial - 2 Shift | 6771 | 1037 | 2620 | Warehouse
Industrial - 3 Shift | 8760 | 1037 | 3466 | Warehouse
Laundromats | 5207 | 1170 | 2015 | Other
Library | 5737 | 1289 | 2220 | Other
Light Manufacturers | 4618 | 1037 | 1787 | Warehouse
Lodging (Hotels/Motels) | 3421 | 769 | 1324 | LargeHotel
Mall Concourse | 4690 | 3013 | 4932 | RetailStandalone
Manufacturing Facility | 4618 | 1037 | 1787 | Warehouse
Medical Offices | 4795 | 1077 | 1855 | SmallOffice
Motion Picture Theatre | 5737 | 1289 | 2220 | Other
Multi-Family (Common Areas) | 3833 | 3833 | 3833 | SmallHotel
Museum | 5737 | 1289 | 2220 | Other
Nursing Homes | 8760 | 4470 | 8760 | Hospital
Office (General Office Types) | 4795 | 1077 | 1855 | SmallOffice
Office/Retail | 4795 | 1077 | 1855 | SmallOffice
Parking Garages & Lots | 6421 | 1442 | 2484 | Other
Penitentiary | 8760 | 4470 | 8760 | LargeHotel
Performing Arts Theatre | 5737 | 1289 | 2220 | Other
Police / Fire Stations (24 Hr) | 6778 | 2774 | 5308 | SmallOffice
Post Office | 4795 | 1077 | 1855 | SmallOffice
Pump Stations | 2241 | 2097 | 4828 | Other
Refrigerated Warehouse | 3604 | 810 | 1394 | Warehouse
Religious Building | 3493 | 785 | 1351 | SmallOffice
Residential (Except Nursing Homes) | 3833 | 3833 | 3833 | SmallHotel
Restaurants | 5264 | 1183 | 2037 | QuickServiceRestaurant
Retail | 5207 | 1170 | 2015 | RetailStripmall
School / University | 5995 | 2357 | 6471 | SecondarySchool
Schools (Jr./Sr. High) | 2241 | 2097 | 4828 | SecondarySchool
Schools (Preschool/Elementary) | 3851 | 865 | 1490 | PrimarySchool
Schools (Technical/Vocational) | 5098 | 2170 | 5620 | SecondarySchool
Small Services | 4795 | 1077 | 1855 | Other
Sports Arena | 5737 | 1289 | 2220 | Other
Town Hall | 5737 | 1289 | 2220 | SmallOffice
Transportation | 6421 | 1442 | 2484 | Other
Warehouse (Not Refrigerated) | 3604 | 810 | 1394 | Warehouse
Waste Water Treatment Plant | 2241 | 2097 | 4828 | Other
Workshop | 4618 | 1037 | 1787 | Warehouse
Source: Maryland TRM V11, pg. 135-136

## Version Log (hidden)
Version Log
Original Author: |  | Meredith Woy | QA/QC Engineer(s): |  | Current Version: | 6.01
Primary Developer: |  | Meredith Woy | Senior Engineer Approval: |  | Date Updated: | 2024-03-25
Version | Date | Reason for Change | Change Description | Contact, Department
1 | 2021-02-19 | Phase V Launch |  | Meredith Woy & Conor McGrail
1.1 | 2021-04-29 | Data Export, DMSHP | Added data export and various fields as needed, added DMSHP measure | Conor McGrail
2.1 | 2021-06-08 | Incentive Updates | Updated to match Potomac Edison's incentive changes | Meredith Woy
2.2 | 2021-11-11 | Various updates | Updated Order Line ID and Sample ID GSHP/WSHP methodology and incentive updates Changed Smart Thermostat Heating Capacity of Furnace from MMBtu/hr to Btu/h Updated PTAC/PTHP Standard vs Non-Standard sizes to reflect TRM definition | Conor McGrail
6 | 2024-01-26 | Phase VI Launch | Updated measures based on V11 TRM. Added ETDF factors and lookup tables. Added new measures | Meredith Dunn
6.01 | 2024-03-25 | Aesthetic Updates | Updated Aesthetics, updated data export | Meredith Dunn